## AEUC Table 5
Location of Wires or Conductors | Neutral | 0 to 0.75 | 0.75 to 22 | 22 to 50 | 50 to 90 | 120 to 150 | 318 | +/- 500 kVDC
Over walkways or land normally accessible only to pedestrians, snowmobiles, and all terrain vehicles not exceeding 3.6m. | 3.7 | 4 | 4.3 | 4.7 | 5 | 5.6 | 9.9 | 6.5
Over rights of way of underground pipelines operating at a pressure of over 700 kilopascals; equipment not exceeding 4.15m. | 4.5 | 4.5 | 4.8 | 5.2 | 5.5 | 6.1 | 9.9 | 7.7
Over land likely to be travelled by road vehicles (including roadways, streets, lanes, alleys, driveways, and entrances); equipment not exceeding 4.15m. ³ | 4.5 | 4.5 | 4.8 | 5.2 | 5.5 | 6.1 | 15.4 | 7.7
Over land likely to be travelled by road vehicles (including highways, roadways, streets, lanes, alleys, driveways, and entrances); equipment not exceeding 5.3m. ⁴ | 5.6 | 5.7 | 6 | 6.4 | 6.7 | 7.3 | 16.6 | 8.9
Over land likely to be travelled by agricultural or other equipment; equipment not exceeding 5.3m. ⁵ | 5.6 | 5.7 | 6 | 6.4 | 6.7 | 7.3 | 12.2 | 8.9
Above top of rails at railway crossings, equipment not exceeding 7.2m. | 7.3 | 7.5 | 7.8 | 8.2 | 8.5 | 9.1 | 11.1 | 10.7

## AEUC Table 7
Wire or Conductor | Min. Horizontal to Building | Min. Vertical to Building | Min. Horizontal to Object | Min. Vertical to Object
Guys communications cables, and drop wires | 0 | 0.08 | 0 | 0.08
0 - 750 V Insulated or grounded | 1 | 2.5 | 0.3 | 0.5
0 - 750 V Enclosed in effectively grounded metallic sheath | 0 | 0 | 0 | 0.8
0 - 750 V Neither insulated or grounded or enclosed in effectively grounded metallic sheath | 1 | 2.5 | 1 | 0.5
0.75 - 22kV Not enclosed in effectively grounded metallic sheath | 3 | 3 | 3 | 3
0.75 - 22kV Enclosed in effectively grounded metallic sheath | 0 | 0 | 0 | 0.08
Over 22kV | 3 | 3.6 | 3 | 3.6

## AEUC Table 7 Output (hidden)
AEUC table 7
Minimum Design Clearances from Wires and Conductors Not Attached to Buildings, Signs, and Similar Plant
(See Rule 10-002 (8) and CSA C22-3 No. 1-10 Clauses 5.7.3.1 & 5.7.3.3.)
System Voltage: kV (AC 3-phase)
Wire or Conductor | Buildings | [7 empty] | Signs, billboards, lamp and traffic sign standards, above ground pipelines, and similar plant
| Horizontal to surface |  |  |  | Vertical to surface |  |  |  | Horizontal to surface |  |  |  | Vertical to surface
| Basic | Voltage Adder | AUEC Total | Design Clearance | Basic | Voltage Adder | AUEC Total | Design Clearance | Basic | Voltage Adder | AUEC Total | Design Clearance | Basic | Voltage Adder | AUEC Total | Design Clearance
| (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m)
Guys, communication cables, and drop wires | 0 | 0 | 0 | 1.2 | 0.08 | 0 | 0.08 | 1.28 | 0 | 0 | 0 | 1.2 | 0.08 | 0 | 0.08 | 1.28
Supply conductors | 1 | 0 | 1 | 2.2 | 2.5 | 0 | 2.5 | 3.7 | 1 | 0 | 1 | 2.2 | 0.5 | 0 | 0.5 | 1.7

## CSA table 2
Locationofwiresor conductors:H=Maximum person,vehicle(incl.load)and equipment heights expected | Guys, messengers, communication, span & lightning protection wires; communication cables | 0-0.75 | 0.75-22 | 22-50 | 50-90 | 90-120 | 120-150 | 150-190 | 219 | 318 | 442
Over land,or alongside land(within the maximum horizontal swing plus flashover distance) likely to be travelled by road vehicles (including roadways, streets, lanes, alleys, driveways and entrances); a H= 4.15m | 4.42 | 4.42 | 4.75 | 5.3 | 5.5 | 5.7 | 6.1 | 6.7 | 7.1 | 8.2 | 9.2
Over land likely to be travelled by agricultural or other equipment, including access roads to farm fields or entrances to farmyards. Over the right-of-way of underground pipelines; H=4.15m | 4.42 | 4.42 | 4.75 | 5.3 | 5.5 | 5.7 | 6.1 | 6.7 | 7.1 | 9.9 | 13.2
Over land likely to be travelled by off-road vehicles, riders on horses or other large animals; H=3.6m | 3.7 | 3.7 | 4.75 | 5.2 | 5.5 | 5.7 | 6.1 | 6.6 | 7.1 | 9.9 | 13.2
Over land within the road right-of way inaccessible to road vehicles (other than requirements in RowsI-III); H=2.9m | 3 | 3.4 | 4.15 | 4.6 | 4.9 | 5.1 | 5.5 | 6 | 6.5 | 7.5 | 8.5
Over walkways or land normally accessible only to pedestrians alone, snowmobiles, and personal use ATV; H=2.4m | 2.5 | 3.1 | 3.4 | 3.7 | 4 | 4.2 | 4.6 | 5.1 | 5.6 | 6.6 | 7.6
Above top of rails at railway crossings;a H=6.7m | 7.3 | 7.3 | 7.6 | 8.1 | 8.4 | 8.6 | 9 | 9.5 | 10 | 11 | 12

## Sheet1 (hidden)
CSA C22-3 No. 1-20 Table 2
Minimum Vertical Design Clearances above Ground or Rails, ac
(See clauses 5.3.1.1, 5.7.4.1 and A.5.3.1 and tables 9 and 11.)
System Voltage: 138 kV (AC 3-phase) Site Elevation: m
|  | Guys, messengers, communication, span & lightning protection wires; communication cables |  |  |  |  | Open Supply Conductors and Service Conductors, ac, kV
>50 <=90
|  | Col II |  |  |  |  | Col VI
Row |  | Basic | Re-pave Adder | Snow Adder | CSA Total | Design Clearance | Basic | Altitude Adder | Re-pave Adder | Snow Adder | CSA Total | Design Clearance
|  | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m) | (m)
I | Over land, or alongside land (within the maximum horizontal swing plus flashover distance) likely to be travelled by road vehicles (including roadways, streets, lanes, alleys, driveways and enterances); H = 4.15m | 4.42 | 0.225 |  | 4.645 | 5.85 | 5.5 | 0.055 | 0.225 |  | 5.78 | 6.98
II | Over or land likely to be travelled by agricultural or other equipment, including access roads to farm fields or entrances to farmyards. Over the right-of-way of underground pipelines; H = 4.15m | 4.42 |  | 0.6 | 5.02 | 6.22 | 5.5 | 0.055 |  | 0.6 | 6.155 | 7.36
III | Over land likely to be travelled by off-road vehicles, riders on horses or other large animals; H = 3.6m | 3.7 |  | 0.6 | 4.3 | 5.5 | 5.5 | 0.055 |  | 0.6 | 6.155 | 7.36
IV | Over land within the road right-of-way inaccessible to road vehicles; H = 2.9m | 3 | 0.225 | 0.6 | 3.825 | 5.03 | 4.9 | 0.049 | 0.225 | 0.6 | 5.774 | 6.98
V | Over walkways or land normally accessible only to pedestrians, snowmobiles, and personal-use all-terrain vehicles; H = 2.4m | 2.5 |  | 0.6 | 3.1 | 4.3 | 4 | 0.04 |  | 0.6 | 4.64 | 5.84
VI | Above top of rails at railway crossings; H = 6.7m | 7.3 | 0.3 |  | 7.6 | 8.8 | 8.4 | 0.084 | 0.3 |  | 8.784 | 9.99
Notes:
1. Re-pave addition to CSA C22.3 No.1 clause 5.3.1.1 (c) & (d).
2. Snow addition to CSA C22.3 No.1 clause 5.3.1.1 (e) table D1.
3. Altitude addition to CSA C22.3 No.1 clause 5.3.1.1 (b).
4. For places that permit the combined vehicle and load height to exceed 4.15 m, the applicable clearance specified in rows I and II shall be increased by the amount by which the allowable combined vehicle and load height exceeds 4.15 m. E.g. High road corridors, railway operating yards, see clauses 5.3.1.2 and A.5.3.1.2.
5. Where noted, minimum clearances shall be based on induced electrostatic steady-state currents. They shall be calculated considering but not limited to the following; line overvoltage, line and conductor configuration, conductor diameter, largest expected vehicle, and line-to-road crossing angle.

## CSA table 5
Type of equipment | Location of equipment | 0–750V | >0.75kV<22kV | >22kV<50kV | >50kV<90kV
Live or exposed current-carrying parts of supply equipment (e.g., cable terminals, arresters, line switches) and ungrounded cases of supply equipment (e.g., transformers, regulators, capacitors) | Areas accessible to pedestrians only | 3 | 3.4 | 3.7 | 4
Live or exposed current-carrying parts of supply equipment (e.g., cable terminals, arresters, line switches) and ungrounded cases of supply equipment (e.g., transformers, regulators, capacitors) | Areas likely to be travelled by vehicles | 4.4 | 4.7 | 5.2 | 5.5
Effectively grounded cases of supply equipment (e.g., transformers, regulators, capacitors) | Areas accessible to pedestrians only | 3 | 3 | 3 | 3
Effectively grounded cases of supply equipment (e.g., transformers, regulators, capacitors) | Areas likely to be travelled by vehicles | 4.4 | 4.4 | 4.4 | 4.4

## CSA table 3
Crossing Class | Type of waterways crossed: A = water areas D = water depth W = water width H = reference vessel height* | Guys; messengers; communication, span, and lightning protection wires; communication cables | 0-22 | >22<50 | >50<90 | >90<150 | >150 + 0.01m/kV over 150kV
0 | Minor Waterways | 4.42 | 4.75 | 5.2 | 5.5 | 6.1 | 6.1
1 | Shallow or fast-moving waterways capable of being used by canoes and paddleboats in isolated areas where motorboats are not expected Creeks and streams: W = 3—50 m and D < 1 m Ponds: A < 8 ha and D < 1m H = 4.0 m | 5 | 6 | 6.3 | 6.7 | 7.3 | 7.3
2 | Shallow or fast-moving waterways capable of being used by motorboats with antennas and unable to support masted vessels Creeks and streams: W = 3—50 m and D < 1 m Ponds: A < 8 ha and D < 1m H = 6.0 m | 7 | 8 | 8.3 | 8.7 | 9.3 | 9.3
3 | Small lakes and rivers used by masted vessels Rivers: W = 3—50 m and D > I m Ponds and lakes: A < 8 ha and D > 1m H = 8.0 m | 9 | 10 | 10.3 | 10.7 | 11.3 | 11.3
4 | Small resort akes, medium-sized rivers and reservoirs, rivers connecting lakes, and crossings adjacent to bridges and roads Rivers: W = 50-500 m Lakes/reservoirs: 8 ha < A < 80 ha H = 10.0 m | 11 | 12 | 12.3 | 12.7 | 13.3 | 13.3
5 | Large lakes, reservoirs, and main rivers in resort areas Rivers: W > 500 m Lakes/reservoirs 80 ha < A < 800 ha H = 12.0 m | 13 | 14 | 14.3 | 14.7 | 15.3 | 15.3
6 | Main lakes on main navigation routes and marinas > 800 ha H = 14.0 m | 15 | 16 | 16.3 | 16.7 | 17.3 | 17.3
7 | Federally maintained commercial channels, rivers, harbours, or herita e canals

## CSA table 6
Wire closest to tracks | Main tracks | Siding
Guys; messengers; communication, span, and lightning protection wires; communication cables | 2.5 | 1.9
Open supply-line conductors and service conductors of 0—750 V and effectively grounded continuous metallic sheathed cables of all voltages | 2.5 | 1.9
AC > 0.75 < 22 kV | 2.7 | 2.1
AC > 22 < 50 kV | 3.2 | 2.6
AC > 50 < 90 kV | 3.5 | 2.9
AC > 90 < 120 kV | 3.8 | 3.2
AC > 120 < 150 kV | 4.1 | 3.5
AC Supply conductors > 150 kV +0.01m/kV over 150kV | 4.1 | 3.5

## CSA table 7
Tracks | Minimum horizontal separation, m
Main tracks (straight, level runs) | 2.5
Sidings (straight, level runs) | 1.9

## CSA table 9
Wire or Conductor | Buildings Horiz. | Buildings Vertical | To signs, billboards, lamp and traffic sign standards, and similar plant Horiz. | To signs, billboards, lamp and traffic sign standards, and similar plant Vertical
Guys, communication cables, and drop wires | 0 | 0.08 | 0 | 0.08
0-0.75kV | 1 | 2.5 | 0.3 | 0.5
| 0 | 0 | 0 | 0.08
| 1 | 2.5 | 1 | 0.5
>0.75kV<=22kV | 0 | 0 | 0 | 0.08
| 2 | 3 | 2 | 2.5
>22kV | 2 | 3.6 | 2 | 3.6

## CSA table 10
Supply conductor | Readily Accessible Conductor attached to bridge (Horizontal) | Readily Accessible Conductor not attached (Horizontal) | Readily Accessible Conductor Attached to Bridge Over Bridge (Vertical) | Readily Conductor Attached to Bridge Accessible Under Bridge (Vertical) | Readily Accessible Conductor not Attached Over Bridge (Vertical) | Readily Accessible Conductor not Attached Under Bridge (Vertical) | Conductor attached to bridge (Horizontal) | Conductor not attached (Horizontal) | Inaccessible Conductor Attached to Bridge Over Bridge (Vertical) | Inaccessible Conductor Attached to Bridge Under Bridge (Vertical) | Inaccessible Conductor not Attached Over Bridge (Vertical) | Inaccessible Conductor not Attached Under Bridge (Vertical)
0-750 v | 1.2 | 1.2 | 2.5 | 0.3 | 2.5 | 0.3 | 0.15 | 0.3 | 0.9 | 1.5 | 2.5 | 0.3
> 0.75 < 22 kV | 1.5 | 1.5 | 3 | 0.9 | 3 | 0.9 | 0.5 | 0.6 | 1.2 | 0.5 | 2.7 | 0.9
> 22 < 50 kV | 1.8 | 1.8 | 3.3 | 1.2 | 3.3 | 1.2 | 0.9 | 0.9 | 1.5 | 0.9 | 3 | 1.2
> 50 kV ac + 0.010 m/kV over 50 kV | 1.8 | 1.8 | 3.3 | 1.2 | 3.3 | 1.2 | 0.9 | 0.9 | 1.5 | 0.9 | 3 | 1.2
> 50 kV dc + 0.005 m/kV over 50 kV | 1.8 | 1.8 | 3.3 | 1.2 | 3.3 | 1.2 | 0.9 | 0.9 | 1.5 | 0.9 | 3 | 1.2

## CSA table 11
Equipment or Conductors | A — Measured in any direction from the water level, edge of pool, or diving platform | B — Measured vertically over land
Supply equipment | 4.6 | See Clause 5.3.2 and Table 5
Guys, messengers, span wires, communication circuits, secondary cable 0–750 V, and multi-grounded neutral conductors | 4.6 | See Clause 5.3.1 and Table 2 and Table 4
Other supply conductors ≤ 22kV | 6.7 | See Clause 5.3.1 and Table 2 and Table 5
Supply conductors > 22 kV and ≤ 150 kV (6.7 + 0.01 m/kV above 22kV) | 6.7 | See Clause 5.3.1 and Table 2 and Table 6
Supply conductors > 150 kV | 8 | See Clause 5.3.1 and Table 2 and Table 7

## CSA table 13
Type of line wire, cable, or other plant being crossed over | Guys, span wires, aerial grounding conductors, and communication wires and cables | AC 0-0.75 | AC < 0.75 ≤ 22 | AC < 22 ≤ 50 | AC < 50 ≤ 90 | AC < 90 ≤ 120 | AC < 120 ≤ 150 | AC < 150 ≤ 190 | AC < 190 ≤ 220 | AC < 220 ≤ 320 | AC < 320 ≤ 425
Communication wires and cables | 0.2 | 0.3 | 0.6 | 0.9 | 1.2 | 1.5 | 1.8 | 2.4 | 2.7 | 3.9 | 4.6
AC 0-0.75 |  | 0.3 | 0.3 | 0.7 | 1 | 1.2 | 1.6 | 2.1 | 2.6 | 3.7 | 4.4
AC < 0.75 ≤ 22 |  | 0.3 | 0.4 | 0.8 | 1.1 | 1.3 | 1.7 | 2.3 | 2.7 | 3.8 | 4.5
AC < 22 ≤ 50 |  | 0.7 | 0.8 | 0.9 | 1.2 | 1.4 | 1.9 | 2.4 | 2.8 | 3.9 | 4.7
AC < 50 ≤ 90 |  |  |  |  | 1.3 | 1.6 | 2.1 | 2.6 | 3 | 4.1 | 4.9
AC < 90 ≤ 120 | [5 empty] | 1.8 | 2.2 | 2.8 | 3.2 | 4.3 | 5.1
AC < 120 ≤ 150 | [6 empty] | 2.4 | 2.9 | 3.4 | 4.5 | 5.2
AC < 150 ≤ 190 | [7 empty] | 3.2 | 3.6 | 4.7 | 5.4
AC < 190 ≤ 220 | [8 empty] | 3.7 | 4.8 | 5.6
AC < 220 ≤ 320 | [9 empty] | 5.4 | 6.1
AC < 320 ≤ 425 | [10 empty] | 6.7
Guys, span wires, and aerial grounding wires | 0.2 | 0.2 | 0.5 | 0.8 | 1.2 | 1.5 | 1.8 | 2.4 | 2.7 | 3.4 | 4.6

## CSA table 14
Type of plant being crossed over | Communication conductors and cables, span and grounding wires carried aerially | 0 – 750V | >0.75kV<22kV | >22kV<50kV | >50kV<90kV | >90kV<120kV | >120kV<150kV | >150kV<190kV | >190kV<220kV | >220kV<320kV | >320kV<425kV
Aerial tramways Gondolas and similar apparatus providing a roof over passengers | 0.15 | 0.15 | 0.5 | 0.8 | 1.2 | 1.5 | 1.8 | 2.4 | 2.7 | 3.9 | 4.6
Chairlifts, T-bars, and similar apparatus or towers of any type of aerial tramway | 1.7 | 1.7 | 2 | 2.3 | 2.7 | 3 | 3.4 | 3.9 | 4.3 | 5.4 | 6

## CSA C22.3 No.1 Table D2
Province | Location | For Lookup | Elevation, m | Mean annual maximum snow depth, m | Tmin 50 (C) | Tmax 50 (C) | V10min50 (km/h) | Vg50 (km/h) | Latitude | Longitude
British Columbia | 100 Mile House | British Columbia 100 Mile House | 1040 | 0.6 | -50 | 38 | 83 | 116 | 51.65 | -121.28
British Columbia | Abbotsford | British Columbia Abbotsford | 70 | 0.5 | -22 | 40 | 96 | 135 | 49.05 | -122.33
British Columbia | Agassiz | British Columbia Agassiz | 15 | 0.6 | -23 | 40 | 94 | 132 | 49.23 | -121.77
British Columbia | Alberni | British Columbia Alberni | 12 | 0.6 | -22 | 41 | 80 | 113 | 49.27 | -124.8
British Columbia | Ashcroft | British Columbia Ashcroft | 305 | 0.4 | -46 | 41 | 90 | 126 | 50.72 | -121.28
British Columbia | Bamfield | British Columbia Bamfield | 20 | 0.2 | -13 | 35 | 100 | 141 | 48.83 | -125.13
British Columbia | Beatton River | British Columbia Beatton River | 840 | 0.8 | -51 | 34 | 80 | 109 | 57.38 | -121.4
British Columbia | Bella Bella | British Columbia Bella Bella | 25 | 0.6 | -19 | 34 | 104 | 146 | 52.16 | -128.14
British Columbia | Bella Coola | British Columbia Bella Coola | 40 | 1.1 | -29 | 38 | 98 | 137 | 52.37 | -126.75
British Columbia | Burns Lake | British Columbia Burns Lake | 755 | 0.8 | -50 | 36 | 80 | 111 | 54.23 | -125.75
British Columbia | Cache Creek | British Columbia Cache Creek | 455 | 0.4 | -46 | 41 | 86 | 120 | 50.8 | -121.32
British Columbia | Campbell River | British Columbia Campbell River | 20 | 0.7 | -21 | 38 | 96 | 135 | 50.02 | -125.24
British Columbia | Carmi | British Columbia Carmi | 845 | 0.8 | -42 | 39 | 84 | 118 | 49.5 | -119.12
British Columbia | Castlegar | British Columbia Castlegar | 430 | 1 | -28 | 41 | 80 | 112 | 49.32 | -117.67
British Columbia | Chetwynd | British Columbia Chetwynd | 605 | 0.6 | -53 | 36 | 90 | 124 | 55.7 | -121.63
British Columbia | Chilliwack | British Columbia Chilliwack | 10 | 0.5 | -23 | 40 | 96 | 135 | 49.17 | -121.95
British Columbia | Comox | British Columbia Comox | 15 | 0.6 | -19 | 39 | 96 | 135 | 49.68 | -124.93
British Columbia | Courtenay | British Columbia Courtenay | 10 | 0.6 | -19 | 39 | 96 | 135 | 49.68 | -124.98
British Columbia | Cranbrook | British Columbia Cranbrook | 910 | 0.7 | -43 | 40 | 80 | 112 | 49.5 | -115.77
British Columbia | Crescent Valley | British Columbia Crescent Valley | 585 | 1 | -38 | 41 | 80 | 112 | 49.45 | -117.55
British Columbia | Crofton | British Columbia Crofton | 5 | 0.4 | -16 | 38 | 85 | 120 | 48.87 | -123.65
British Columbia | Dawson Creek | British Columbia Dawson Creek | 665 | 0.6 | -52 | 36 | 92 | 126 | 55.77 | -120.23
British Columbia | Dease Lake | British Columbia Dease Lake | 800 | 0.7 | -50 | 34 | 80 | 110 | 58.44 | -130
British Columbia | Dog Creek | British Columbia Dog Creek | 450 | 0.4 | -49 | 38 | 80 | 112 | 51.58 | -122.3
British Columbia | Duncan | British Columbia Duncan | 10 | 0.4 | -22 | 40 | 80 | 113 | 48.78 | -123.7
British Columbia | Elko | British Columbia Elko | 1065 | 0.8 | -43 | 39 | 80 | 112 | 49.3 | -115.12
British Columbia | Fernie | British Columbia Fernie | 1010 | 1.1 | -46 | 38 | 80 | 111 | 49.5 | -115.07
British Columbia | Fort Nelson | British Columbia Fort Nelson | 465 | 0.6 | -51 | 36 | 80 | 109 | 58.83 | -122.7
British Columbia | Fort St. John | British Columbia Fort St. John | 685 | 0.7 | -50 | 36 | 95 | 130 | 56.25 | -120.85
British Columbia | Glacier | British Columbia Glacier | 1145 | 2.2 | -40 | 35 | 80 | 111 | 51.27 | -117.52
British Columbia | Golden | British Columbia Golden | 790 | 0.9 | -48 | 40 | 80 | 111 | 51.3 | -116.97
British Columbia | Gold River | British Columbia Gold River | 120 | 0.7 | -22 | 40 | 80 | 113 | 49.78 | -126.05
British Columbia | Grand Forks | British Columbia Grand Forks | 565 | 0.7 | -43 | 42 | 85 | 119 | 49.03 | -118.45
British Columbia | Greenwood | British Columbia Greenwood | 745 | 0.8 | -45 | 43 | 85 | 119 | 49.1 | -118.68
British Columbia | Hope | British Columbia Hope | 40 | 0.7 | -26 | 40 | 108 | 152 | 49.38 | -121.44
British Columbia | Jordan River | British Columbia Jordan River | 20 | 0.3 | -13 | 32 | 118 | 167 | 48.42 | -124.05
British Columbia | Kamloops | British Columbia Kamloops | 355 | 0.4 | -40 | 42 | 90 | 126 | 50.67 | -120.32
British Columbia | Kaslo | British Columbia Kaslo | 545 | 0.7 | -30 | 38 | 80 | 112 | 49.92 | -116.92
British Columbia | Kelowna | British Columbia Kelowna | 350 | 0.4 | -35 | 41 | 82 | 115 | 49.88 | -119.48
British Columbia | Kimberley | British Columbia Kimberley | 1090 | 0.7 | -40 | 40 | 80 | 112 | 49.68 | -115.98
British Columbia | Kitimat Plant | British Columbia Kitimat Plant | 15 | 1.3 | -30 | 38 | 98 | 137 | 54.05 | -128.63
British Columbia | Kitimat Townsite | British Columbia Kitimat Townsite | 130 | 1.5 | -30 | 38 | 98 | 137 | 54.07 | -128.65
British Columbia | Ladysmith | British Columbia Ladysmith | 80 | 0.6 | -16 | 38 | 80 | 113 | 48.99 | -123.82
British Columbia | Langford | British Columbia Langford | 80 | 0.4 | -16 | 38 | 89 | 126 | 48.45 | -123.5
British Columbia | Lillooet | British Columbia Lillooet | 245 | 0.5 | -35 | 43 | 88 | 123 | 50.68 | -121.93
British Columbia | Lytton | British Columbia Lytton | 325 | 0.7 | -34 | 44 | 98 | 137 | 50.23 | -121.57
British Columbia | Mackenzie | British Columbia Mackenzie | 765 | 1.2 | -52 | 36 | 80 | 110 | 55.3 | -123.08
British Columbia | Masset | British Columbia Masset | 10 | 0.4 | -19 | 29 | 117 | 164 | 54.02 | -132.1
British Columbia | McBride | British Columbia McBride | 730 | 1 | -53 | 38 | 85 | 118 | 53.3 | -120.17
British Columbia | McLeod Lake | British Columbia McLeod Lake | 695 | 1 | -52 | 36 | 80 | 110 | 54.98 | -123.03
British Columbia | Merritt | British Columbia Merritt | 570 | 0.4 | -43 | 40 | 80 | 112 | 50.1 | -120.78
British Columbia | Mission City | British Columbia Mission City | 45 | 0.6 | -22 | 40 | 96 | 135 | 49.13 | -122.3
British Columbia | Montrose | British Columbia Montrose | 615 | 1 | -37 | 41 | 86 | 120 | 49.08 | -117.58
British Columbia | Nakusp | British Columbia Nakusp | 445 | 1 | -28 | 41 | 80 | 112 | 50.23 | -117.8
British Columbia | Nanaimo | British Columbia Nanaimo | 15 | 0.5 | -19 | 38 | 88 | 124 | 49.17 | -123.93
British Columbia | Nelson | British Columbia Nelson | 600 | 1 | -30 | 40 | 80 | 112 | 49.48 | -117.28
British Columbia | Ocean Falls | British Columbia Ocean Falls | 10 | 0.9 | -23 | 38 | 99 | 139 | 52.35 | -127.7
British Columbia | Osoyoos | British Columbia Osoyoos | 285 | 0.3 | -28 | 42 | 84 | 118 | 49.03 | -119.5
British Columbia | Parksville | British Columbia Parksville | 40 | 0.5 | -18 | 36 | 88 | 124 | 49.32 | -124.33
British Columbia | Penticton | British Columbia Penticton | 350 | 0.3 | -30 | 41 | 86 | 120 | 49.5 | -119.58
British Columbia | Port Alberni | British Columbia Port Alberni | 15 | 0.6 | -22 | 41 | 80 | 113 | 49.23 | -124.8
British Columbia | Port Alice | British Columbia Port Alice | 25 | 0.3 | -14 | 35 | 80 | 113 | 50.38 | -127.45
British Columbia | Port Hardy | British Columbia Port Hardy | 5 | 0.2 | -15 | 31 | 104 | 147 | 50.7 | -127.42
British Columbia | Port McNeill | British Columbia Port McNeill | 5 | 0.3 | -15 | 33 | 99 | 139 | 50.58 | -127.1
British Columbia | Port Renfrew | British Columbia Port Renfrew | 20 | 0.3 | -13 | 35 | 108 | 153 | 48.56 | -124.4
British Columbia | Powell River | British Columbia Powell River | 10 | 0.4 | -17 | 36 | 105 | 148 | 49.83 | -124.52
British Columbia | Prince George | British Columbia Prince George | 580 | 0.8 | -51 | 38 | 87 | 121 | 53.92 | -122.75
British Columbia | Prince Rupert | British Columbia Prince Rupert | 20 | 0.4 | -26 | 32 | 110 | 154 | 54.32 | -130.32
British Columbia | Princeton | British Columbia Princeton | 655 | 0.7 | -40 | 40 | 85 | 119 | 49.5 | -120.51
British Columbia | Qualicum Beach | British Columbia Qualicum Beach | 10 | 0.5 | -18 | 36 | 88 | 124 | 49.35 | -124.45
British Columbia | Queen Charlotte City | British Columbia Queen Charlotte City | 35 | 0.4 | -18 | 31 | 117 | 164 | 53.26 | -132.08
British Columbia | Quesnel | British Columbia Quesnel | 475 | 0.7 | -51 | 39 | 84 | 117 | 52.98 | -122.48
British Columbia | Revelstoke | British Columbia Revelstoke | 440 | 1.7 | -38 | 41 | 88 | 122 | 50.98 | -118.2
British Columbia | Salmon Arm | British Columbia Salmon Arm | 425 | 0.8 | -38 | 41 | 88 | 123 | 50.7 | -119.28
British Columbia | Sandspit | British Columbia Sandspit | 5 | 0.4 | -17 | 29 | 121 | 170 | 53.25 | -131.82
British Columbia | Sechelt | British Columbia Sechelt | 25 | 0.4 | -16 | 34 | 95 | 134 | 49.47 | -123.75
British Columbia | Sidney | British Columbia Sidney | 10 | 0.3 | -16 | 37 | 88 | 124 | 48.65 | -123.4
British Columbia | Smithers | British Columbia Smithers | 500 | 0.8 | -47 | 37 | 88 | 122 | 54.78 | -127.17
British Columbia | Smith River | British Columbia Smith River | 660 | 0.7 | -56 | 34 | 80 | 109 | 59.88 | -126.43
British Columbia | Sooke | British Columbia Sooke | 20 | 0.3 | -16 | 37 | 104 | 147 | 48.38 | -123.72
British Columbia | Squamish | British Columbia Squamish | 5 | 0.7 | -18 | 40 | 98 | 138 | 49.7 | -123.15
British Columbia | Stewart | British Columbia Stewart | 10 | 1.9 | -29 | 35 | 80 | 111 | 55.93 | -129.98
British Columbia | Tahsis | British Columbia Tahsis | 25 | 0.3 | -13 | 39 | 80 | 113 | 49.93 | -126.65
British Columbia | Taylor | British Columbia Taylor | 515 | 0.5 | -50 | 36 | 95 | 130 | 56.2 | -120.69
British Columbia | Terrace | British Columbia Terrace | 60 | 1.3 | -30 | 39 | 98 | 136 | 54.52 | -128.6
British Columbia | Tofino | British Columbia Tofino | 10 | 0.3 | -13 | 36 | 110 | 156 | 49.12 | -125.88
British Columbia | Trail | British Columbia Trail | 440 | 1 | -34 | 42 | 85 | 119 | 49.1 | -117.7
British Columbia | Ucluelet | British Columbia Ucluelet | 5 | 0.2 | -13 | 36 | 110 | 156 | 48.93 | -125.55
Greater Vancouver | Burnaby (Simon Fraser Univ.) | Greater Vancouver Burnaby (Simon Fraser Univ.) | 330 | 0.7 | -19 | 37 | 100 | 141 | 49.28 | -122.92
Greater Vancouver | Cloverdale | Greater Vancouver Cloverdale | 10 | 0.6 | -20 | 38 | 88 | 124 | 49.1 | -122.73
Greater Vancouver | Haney | Greater Vancouver Haney | 10 | 0.6 | -21 | 39 | 88 | 124 | 49.22 | -122.6
Greater Vancouver | Ladner | Greater Vancouver Ladner | 3 | 0.3 | -19 | 34 | 88 | 124 | 49.08 | -123.08
Greater Vancouver | Langley | Greater Vancouver Langley | 15 | 0.6 | -20 | 39 | 88 | 124 | 49.1 | -122.65
Greater Vancouver | New Westminster | Greater Vancouver New Westminster | 10 | 0.5 | -21 | 38 | 88 | 124 | 49.22 | -122.92
Greater Vancouver | North Vancouver | Greater Vancouver North Vancouver | 135 | 0.7 | -20 | 36 | 88 | 124 | 49.32 | -123.07
Greater Vancouver | Richmond | Greater Vancouver Richmond | 5 | 0.4 | -21 | 36 | 88 | 124 | 49.17 | -123.1
Greater Vancouver | Surrey (88 Ave. & 156 St.) | Greater Vancouver Surrey (88 Ave. & 156 St.) | 90 | 0.6 | -22 | 39 | 88 | 124 | 49.16 | -122.79
Greater Vancouver | Vancouver (City Hall) | Greater Vancouver Vancouver (City Hall) | 40 | 0.4 | -19 | 36 | 88 | 124 | 49.25 | -123.12
Greater Vancouver | Vancouver (Granville & 41 Ave.) | Greater Vancouver Vancouver (Granville & 41 Ave.) | 120 | 0.4 | -19 | 36 | 88 | 124 | 49.23 | -123.14
Greater Vancouver | West Vancouver | Greater Vancouver West Vancouver | 45 | 0.6 | -16 | 36 | 88 | 124 | 49.33 | -123.17
Greater Vancouver | Vernon | Greater Vancouver Vernon | 405 | 0.5 | -35 | 41 | 85 | 119 | 50.3 | -119.27
Greater Vancouver | Victoria (Gonzales Hts) | Greater Vancouver Victoria (Gonzales Hts) | 65 | 0.4 | -14 | 38 | 112 | 158 | 48.42 | -123.32
Greater Vancouver | Victoria (Mt Tolmie) | Greater Vancouver Victoria (Mt Tolmie) | 125 | 0.5 | -16 | 38 | 100 | 141 | 48.47 | -123.33
Greater Vancouver | Victoria | Greater Vancouver Victoria | 10 | 0.3 | -16 | 38 | 100 | 141 | 48.43 | -123.37
Greater Vancouver | Whistler | Greater Vancouver Whistler | 665 | 2.2 | -31 | 39 | 78 | 110 | 50.12 | -122.96
Greater Vancouver | White Rock | Greater Vancouver White Rock | 30 | 0.5 | -17 | 35 | 88 | 124 | 49.02 | -122.8
Greater Vancouver | Williams Lake | Greater Vancouver Williams Lake | 615 | 0.6 | -49 | 40 | 86 | 120 | 52.13 | -122.15
Greater Vancouver | Youbou | Greater Vancouver Youbou | 200 | 0.8 | -19 | 40 | 80 | 113 | 48.88 | -124.2
Alberta | Athabasca | Alberta Athabasca | 515 | 0.4 | -50 | 36 | 85 | 116 | 54.72 | -113.28
Alberta | Banff | Alberta Banff | 1400 | 1 | -50 | 36 | 80 | 111 | 51.17 | -115.57
Alberta | Barrhead | Alberta Barrhead | 645 | 0.5 | -54 | 37 | 88 | 121 | 54.13 | -114.4
Alberta | Beaverlodge | Alberta Beaverlodge | 730 | 0.7 | -50 | 36 | 94 | 129 | 55.22 | -119.43
Alberta | Brooks | Alberta Brooks | 760 | 0.4 | -47 | 39 | 99 | 137 | 50.58 | -111.88
Alberta | Calgary | Alberta Calgary | 1045 | 0.3 | -43 | 37 | 99 | 137 | 51.05 | -114.08
Alberta | Campsie | Alberta Campsie | 660 | 0.5 | -54 | 37 | 88 | 121 | 54.13 | -114.65
Alberta | Camrose | Alberta Camrose | 740 | 0.6 | -50 | 37 | 90 | 124 | 53.02 | -112.83
Alberta | Canmore | Alberta Canmore | 1320 | 1 | -48 | 37 | 89 | 123 | 51.09 | -115.35
Alberta | Cardston | Alberta Cardston | 1130 | 0.4 | -43 | 39 | 108 | 150 | 49.2 | -113.3
Alberta | Claresholm | Alberta Claresholm | 1030 | 0.4 | -45 | 38 | 110 | 153 | 50.03 | -113.58
Alberta | Cold Lake | Alberta Cold Lake | 540 | 0.5 | -49 | 37 | 89 | 121 | 54.45 | -110.17
Alberta | Coleman | Alberta Coleman | 1320 | 0.8 | -47 | 36 | 90 | 125 | 49.63 | -114.5
Alberta | Coronation | Alberta Coronation | 790 | 0.6 | -48 | 39 | 91 | 125 | 52.08 | -111.45
Alberta | Cowley | Alberta Cowley | 1175 | 0.5 | -48 | 37 | 135 | 188 | 49.57 | -114.08
Alberta | Drumheller | Alberta Drumheller | 685 | 0.4 | -48 | 39 | 95 | 131 | 51.47 | -112.7
Alberta | Edmonton | Alberta Edmonton | 645 | 0.5 | -48 | 37 | 92 | 126 | 53.55 | -113.47
Alberta | Edson | Alberta Edson | 920 | 0.6 | -50 | 37 | 88 | 121 | 53.58 | -116.43
Alberta | Embarras Portage | Alberta Embarras Portage | 220 | 0.7 | -53 | 36 | 80 | 108 | 58.45 | -111.47
Alberta | Fairview | Alberta Fairview | 670 | 0.7 | -52 | 36 | 85 | 116 | 56.07 | -118.38
Alberta | Fort MacLeod | Alberta Fort MacLeod | 945 | 0.4 | -47 | 40 | 110 | 153 | 49.72 | -113.42
Alberta | Fort McMurray | Alberta Fort McMurray | 255 | 0.4 | -51 | 38 | 80 | 108 | 56.73 | -111.38
Alberta | Fort Saskatchewan | Alberta Fort Saskatchewan | 610 | 0.5 | -49 | 37 | 90 | 123 | 53.72 | -113.22
Alberta | Fort Vermilion | Alberta Fort Vermilion | 270 | 0.6 | -57 | 37 | 80 | 108 | 58.4 | -116
Alberta | Grande Prairie | Alberta Grande Prairie | 650 | 0.7 | -52 | 36 | 95 | 130 | 55.17 | -118.8
Alberta | Habay | Alberta Habay | 335 | 0.7 | -55 | 36 | 80 | 108 | 58.83 | -118.73
Alberta | Hardisty | Alberta Hardisty | 615 | 0.5 | -49 | 39 | 94 | 129 | 52.67 | -111.3
Alberta | High River | Alberta High River | 1040 | 0.4 | -46 | 38 | 98 | 136 | 50.58 | -113.87
Alberta | Hinton | Alberta Hinton | 990 | 0.8 | -52 | 37 | 85 | 117 | 53.4 | -117.58
Alberta | Jasper | Alberta Jasper | 1060 | 0.9 | -48 | 37 | 80 | 111 | 52.88 | -118.08
Alberta | Keg River | Alberta Keg River | 420 | 0.7 | -55 | 37 | 80 | 109 | 57.75 | -117.62
Alberta | Lac La Biche | Alberta Lac La Biche | 560 | 0.5 | -52 | 36 | 88 | 120 | 54.77 | -111.97
Alberta | Lacombe | Alberta Lacombe | 855 | 0.6 | -49 | 37 | 92 | 127 | 52.47 | -113.73
Alberta | Lethbridge | Alberta Lethbridge | 910 | 0.4 | -46 | 39 | 108 | 150 | 49.7 | -112.82
Alberta | Manning | Alberta Manning | 465 | 0.7 | -54 | 36 | 80 | 109 | 56.92 | -117.62
Alberta | Medicine Hat | Alberta Medicine Hat | 705 | 0.3 | -49 | 42 | 98 | 136 | 50.05 | -110.67
Alberta | Peace River | Alberta Peace River | 330 | 0.7 | -52 | 36 | 85 | 116 | 56.23 | -117.28
Alberta | Pincher Creek | Alberta Pincher Creek | 1130 | 0.4 | -47 | 37 | 140 | 195 | 49.48 | -113.95
Alberta | Ranfurly | Alberta Ranfurly | 670 | 0.6 | -49 | 38 | 90 | 123 | 53.42 | -111.68
Alberta | Red Deer | Alberta Red Deer | 855 | 0.5 | -48 | 38 | 92 | 127 | 52.27 | -113.8
Alberta | Rocky Mountain House | Alberta Rocky Mountain House | 985 | 0.6 | -47 | 35 | 89 | 123 | 52.37 | -114.92
Alberta | Slave Lake | Alberta Slave Lake | 590 | 0.6 | -50 | 35 | 91 | 124 | 55.28 | -114.77
Alberta | Stettler | Alberta Stettler | 820 | 0.6 | -49 | 34 | 92 | 127 | 52.32 | -112.72
Alberta | Stony Plain | Alberta Stony Plain | 710 | 0.5 | -47 | 36 | 90 | 123 | 53.53 | -114
Alberta | Suffield | Alberta Suffield | 755 | 0.4 | -48 | 40 | 98 | 136 | 50.2 | -111.17
Alberta | Taber | Alberta Taber | 815 | 0.4 | -45 | 39 | 98 | 136 | 49.78 | -112.15
Alberta | Turner Valley | Alberta Turner Valley | 1215 | 0.4 | -46 | 37 | 98 | 136 | 50.67 | -114.28
Alberta | Valleyview | Alberta Valleyview | 700 | 0.7 | -50 | 36 | 80 | 110 | 55.07 | -117.28
Alberta | Vegreville | Alberta Vegreville | 635 | 0.6 | -50 | 37 | 90 | 123 | 53.5 | -112.05
Alberta | Vermilion | Alberta Vermilion | 580 | 0.5 | -49 | 38 | 90 | 123 | 53.37 | -110.85
Alberta | Wagner | Alberta Wagner | 585 | 0.6 | -50 | 36 | 88 | 120 | 55.35 | -114.98
Alberta | Wainwright | Alberta Wainwright | 675 | 0.6 | -49 | 39 | 90 | 123 | 52.82 | -110.87
Alberta | Wetaskiwin | Alberta Wetaskiwin | 760 | 0.6 | -50 | 37 | 92 | 126 | 52.97 | -113.37
Alberta | Whitecourt | Alberta Whitecourt | 690 | 0.6 | -49 | 35 | 86 | 118 | 54.15 | -115.68
Alberta | Wimborne | Alberta Wimborne | 975 | 0.5 | -48 | 38 | 95 | 131 | 51.87 | -113.58
Saskatchewan | Assiniboia | Saskatchewan Assiniboia | 740 | 0.5 | -44 | 41 | 100 | 138 | 49.63 | -105.98
Saskatchewan | Battrum | Saskatchewan Battrum | 700 | 0.4 | -45 | 41 | 100 | 138 | 50.55 | -108.33
Saskatchewan | Biggar | Saskatchewan Biggar | 645 | 0.6 | -48 | 41 | 95 | 130 | 52.07 | -108
Saskatchewan | Broadview | Saskatchewan Broadview | 600 | 0.5 | -46 | 40 | 102 | 139 | 50.37 | -102.58
Saskatchewan | Dafoe | Saskatchewan Dafoe | 530 | 0.5 | -47 | 39 | 89 | 121 | 51.75 | -104.53
Saskatchewan | Dundurn | Saskatchewan Dundurn | 525 | 0.4 | -47 | 41 | 95 | 130 | 51.82 | -106.5
Saskatchewan | Estevan | Saskatchewan Estevan | 565 | 0.5 | -45 | 42 | 104 | 143 | 49.13 | -102.98
Saskatchewan | Hudson Bay | Saskatchewan Hudson Bay | 370 | 0.6 | -47 | 38 | 85 | 115 | 52.85 | -102.38
Saskatchewan | Humboldt | Saskatchewan Humboldt | 565 | 0.6 | -49 | 40 | 88 | 120 | 52.2 | -105.12
Saskatchewan | Island Falls | Saskatchewan Island Falls | 305 | 0.6 | -49 | 38 | 80 | 107 | 55.53 | -102.35
Saskatchewan | Kamsack | Saskatchewan Kamsack | 455 | 0.6 | -46 | 39 | 89 | 121 | 51.57 | -101.9
Saskatchewan | Kindersley | Saskatchewan Kindersley | 685 | 0.4 | -47 | 40 | 100 | 137 | 51.47 | -109.17
Saskatchewan | Lloydminster | Saskatchewan Lloydminster | 645 | 0.6 | -46 | 39 | 95 | 130 | 53.28 | -110
Saskatchewan | Maple Creek | Saskatchewan Maple Creek | 765 | 0.4 | -47 | 41 | 101 | 140 | 49.92 | -109.48
Saskatchewan | Meadow Lake | Saskatchewan Meadow Lake | 480 | 0.5 | -50 | 38 | 89 | 121 | 54.13 | -108.43
Saskatchewan | Melfort | Saskatchewan Melfort | 455 | 0.6 | -47 | 39 | 85 | 116 | 52.87 | -104.62
Saskatchewan | Melville | Saskatchewan Melville | 550 | 0.5 | -46 | 39 | 95 | 130 | 50.92 | -102.8
Saskatchewan | Moose Jaw | Saskatchewan Moose Jaw | 545 | 0.4 | -46 | 42 | 105 | 144 | 50.4 | -105.53
Saskatchewan | Nipawin | Saskatchewan Nipawin | 365 | 0.6 | -49 | 40 | 86 | 117 | 53.37 | -104
Saskatchewan | North Battleford | Saskatchewan North Battleford | 545 | 0.5 | -48 | 40 | 94 | 128 | 52.78 | -108.28
Saskatchewan | Prince Albert | Saskatchewan Prince Albert | 435 | 0.6 | -49 | 39 | 93 | 126 | 53.2 | -105.77
Saskatchewan | Qu'Appelle | Saskatchewan Qu'Appelle | 645 | 0.5 | -46 | 41 | 97 | 133 | 50.55 | -103.88
Saskatchewan | Regina | Saskatchewan Regina | 575 | 0.4 | -46 | 42 | 105 | 144 | 50.45 | -104.62
Saskatchewan | Rosetown | Saskatchewan Rosetown | 595 | 0.5 | -47 | 41 | 99 | 136 | 51.55 | -108
Saskatchewan | Saskatoon | Saskatchewan Saskatoon | 500 | 0.5 | -47 | 41 | 99 | 135 | 52.12 | -106.63
Saskatchewan | Scott | Saskatchewan Scott | 645 | 0.6 | -50 | 40 | 93 | 127 | 52.37 | -108.83
Saskatchewan | Strasbourg | Saskatchewan Strasbourg | 545 | 0.4 | -47 | 41 | 97 | 133 | 51.07 | -104.95
Saskatchewan | Swift Current | Saskatchewan Swift Current | 750 | 0.4 | -45 | 40 | 104 | 143 | 50.28 | -107.8
Saskatchewan | Uranium City | Saskatchewan Uranium City | 265 | 0.6 | -50 | 36 | 84 | 112 | 59.57 | -108.62
Saskatchewan | Weyburn | Saskatchewan Weyburn | 575 | 0.5 | -45 | 42 | 100 | 137 | 49.67 | -103.85
Saskatchewan | Yorkton | Saskatchewan Yorkton | 510 | 0.6 | -46 | 39 | 90 | 123 | 51.22 | -102.47
Manitoba | Beausejour | Manitoba Beausejour | 245 | 0.6 | -45 | 39 | 88 | 120 | 50.07 | -96.52
Manitoba | Boissevain | Manitoba Boissevain | 510 | 0.7 | -44 | 40 | 102 | 140 | 49.23 | -100.05
Manitoba | Brandon | Manitoba Brandon | 395 | 0.6 | -45 | 41 | 102 | 139 | 49.83 | -99.95
Manitoba | Churchill | Manitoba Churchill | 10 | 0.6 | -47 | 36 | 102 | 134 | 58.75 | -94.12
Manitoba | Dauphin | Manitoba Dauphin | 295 | 0.6 | -44 | 39 | 90 | 122 | 51.15 | -100.05
Manitoba | Flin Flon | Manitoba Flin Flon | 300 | 0.7 | -47 | 37 | 86 | 116 | 54.77 | -101.88
Manitoba | Gimli | Manitoba Gimli | 220 | 0.6 | -46 | 39 | 90 | 122 | 50.64 | -96.99
Manitoba | Island Lake | Manitoba Island Lake | 240 | 0.8 | -46 | 37 | 86 | 115 | 53.87 | -94.67
Manitoba | Lac du Bonnet | Manitoba Lac du Bonnet | 260 | 0.6 | -47 | 39 | 85 | 115 | 50.27 | -96.06
Manitoba | Lynn Lake | Manitoba Lynn Lake | 350 | 0.7 | -49 | 37 | 83 | 111 | 56.85 | -101.05
Manitoba | Morden | Manitoba Morden | 300 | 0.7 | -42 | 42 | 103 | 141 | 49.18 | -98.1
Manitoba | Neepawa | Manitoba Neepawa | 365 | 0.7 | -44 | 39 | 95 | 129 | 50.23 | -99.47
Manitoba | Pine Falls | Manitoba Pine Falls | 220 | 0.6 | -47 | 39 | 87 | 118 | 50.57 | -96.22
Manitoba | Portage La Prairie | Manitoba Portage La Prairie | 260 | 0.6 | -43 | 40 | 98 | 133 | 50 | -98.29
Manitoba | Rivers | Manitoba Rivers | 465 | 0.6 | -45 | 40 | 99 | 135 | 50.03 | -100.23
Manitoba | Sandilands | Manitoba Sandilands | 365 | 0.7 | -47 | 39 | 89 | 121 | 49.36 | -96.3
Manitoba | Selkirk | Manitoba Selkirk | 225 | 0.6 | -55 | 39 | 89 | 121 | 50.15 | -96.87
Manitoba | Split Lake | Manitoba Split Lake | 175 | 0.7 | -48 | 38 | 89 | 118 | 56.25 | -96.1
Manitoba | Steinbach | Manitoba Steinbach | 270 | 0.6 | -45 | 39 | 93 | 127 | 49.53 | -96.68
Manitoba | Swan River | Manitoba Swan River | 335 | 0.6 | -46 | 39 | 84 | 114 | 52.14 | -101.27
Manitoba | The Pas | Manitoba The Pas | 270 | 0.7 | -47 | 37 | 89 | 120 | 53.87 | -101.25
Manitoba | Thompson | Manitoba Thompson | 205 | 0.7 | -50 | 38 | 80 | 107 | 55.79 | -97.86
Manitoba | Virden | Manitoba Virden | 435 | 0.6 | -45 | 40 | 102 | 139 | 49.86 | -100.93
Manitoba | Winnipeg | Manitoba Winnipeg | 235 | 0.6 | -44 | 40 | 99 | 135 | 49.89 | -97.15
Ontario | Ailsa Craig | Ontario Ailsa Craig | 230 | 0.7 | -33 | 39 | 98 | 134 | 43.13 | -81.55
Ontario | Ajax | Ontario Ajax | 95 | 0.3 | -31 | 38 | 97 | 132 | 43.85 | -79.03
Ontario | Alexandria | Ontario Alexandria | 80 | 0.7 | -40 | 37 | 90 | 121 | 45.32 | -74.63
Ontario | Alliston | Ontario Alliston | 220 | 0.6 | -36 | 38 | 90 | 122 | 44.15 | -79.87
Ontario | Almonte | Ontario Almonte | 120 | 0.7 | -39 | 38 | 86 | 116 | 45.23 | -76.2
Ontario | Armstrong | Ontario Armstrong | 340 | 0.8 | -50 | 38 | 83 | 112 | 50.3 | -89.03
Ontario | Arnprior | Ontario Arnprior | 85 | 0.7 | -40 | 38 | 88 | 118 | 45.43 | -76.35
Ontario | Atikokan | Ontario Atikokan | 400 | 0.7 | -47 | 39 | 86 | 117 | 48.75 | -91.62
Ontario | Attawapiskat | Ontario Attawapiskat | 10 | 0.8 | -49 | 35 | 94 | 124 | 52.93 | -82.43
Ontario | Aurora | Ontario Aurora | 270 | 0.6 | -34 | 39 | 89 | 121 | 44 | -79.47
Ontario | Bancroft | Ontario Bancroft | 365 | 0.9 | -43 | 38 | 80 | 108 | 45.05 | -77.85
Ontario | Barrie | Ontario Barrie | 245 | 0.7 | -39 | 38 | 88 | 119 | 44.4 | -79.67
Ontario | Barriefield | Ontario Barriefield | 100 | 0.6 | -35 | 37 | 102 | 138 | 44.23 | -76.47
Ontario | Beaverton | Ontario Beaverton | 240 | 0.7 | -39 | 38 | 85 | 115 | 44.43 | -79.15
Ontario | Belleville | Ontario Belleville | 90 | 0.5 | -38 | 38 | 98 | 133 | 44.17 | -77.38
Ontario | Belmont | Ontario Belmont | 260 | 0.5 | -32 | 39 | 102 | 139 | 42.88 | -81.08
Ontario | CFB Borden | Ontario CFB Borden | 225 | 0.7 | -39 | 38 | 88 | 119 | 44.2629 | -79.9011
Ontario | Bracebridge | Ontario Bracebridge | 310 | 0.9 | -43 | 37 | 88 | 119 | 45.03 | -79.3
Ontario | Bradford | Ontario Bradford | 240 | 0.6 | -36 | 38 | 88 | 119 | 44.12 | -79.57
Ontario | Brampton | Ontario Brampton | 215 | 0.4 | -34 | 39 | 94 | 128 | 43.68 | -79.77
Ontario | Brantford | Ontario Brantford | 205 | 0.4 | -33 | 39 | 100 | 136 | 43.13 | -80.27
Ontario | Brighton | Ontario Brighton | 95 | 0.5 | -35 | 38 | 101 | 137 | 44.03 | -77.73
Ontario | Brockville | Ontario Brockville | 85 | 0.7 | -37 | 38 | 92 | 124 | 44.59 | -75.68
Ontario | Burk’s Falls | Ontario Burk’s Falls | 305 | 0.8 | -44 | 38 | 80 | 108 | 45.6199 | -79.4087
Ontario | Burlington | Ontario Burlington | 80 | 0.3 | -30 | 39 | 94 | 128 | 43.32 | -79.8
Ontario | Cambridge | Ontario Cambridge | 295 | 0.5 | -33 | 38 | 96 | 131 | 43.38 | -80.32
Ontario | Campbellford | Ontario Campbellford | 150 | 0.5 | -39 | 38 | 86 | 116 | 44.3 | -77.8
Ontario | Cannington | Ontario Cannington | 255 | 0.7 | -38 | 38 | 85 | 115 | 44.35 | -79.03
Ontario | Carleton Place | Ontario Carleton Place | 135 | 0.7 | -38 | 38 | 86 | 116 | 45.13 | -76.15
Ontario | Cavan | Ontario Cavan | 200 | 0.6 | -36 | 38 | 85 | 115 | 44.2 | -78.47
Ontario | Centralia | Ontario Centralia | 260 | 0.7 | -33 | 38 | 96 | 131 | 43.28 | -81.47
Ontario | Chapleau | Ontario Chapleau | 425 | 1.1 | -48 | 38 | 82 | 110 | 47.83 | -83.4
Ontario | Chatham | Ontario Chatham | 180 | 0.3 | -30 | 39 | 98 | 134 | 42.4 | -82.18
Ontario | Chesley | Ontario Chesley | 275 | 0.8 | -38 | 37 | 96 | 130 | 44.28 | -81.08
Ontario | Clinton | Ontario Clinton | 280 | 0.8 | -34 | 37 | 99 | 135 | 43.62 | -81.53
Ontario | Coboconk | Ontario Coboconk | 270 | 0.7 | -40 | 38 | 82 | 111 | 44.65 | -78.8
Ontario | Cobourg | Ontario Cobourg | 90 | 0.4 | -34 | 38 | 100 | 136 | 43.97 | -78.17
Ontario | Cochrane | Ontario Cochrane | 245 | 0.8 | -48 | 38 | 84 | 112 | 49.07 | -81.02
Ontario | Colborne | Ontario Colborne | 105 | 0.5 | -35 | 38 | 99 | 134 | 44 | -77.88
Ontario | Collingwood | Ontario Collingwood | 190 | 0.8 | -34 | 38 | 94 | 128 | 44.48 | -80.22
Ontario | Cornwall | Ontario Cornwall | 35 | 0.7 | -38 | 37 | 94 | 126 | 45.03 | -74.73
Ontario | Corunna | Ontario Corunna | 185 | 0.3 | -30 | 39 | 98 | 134 | 42.88 | -82.43
Ontario | Deep River | Ontario Deep River | 145 | 0.7 | -43 | 39 | 89 | 120 | 46.1 | -77.5
Ontario | Deseronto | Ontario Deseronto | 85 | 0.6 | -38 | 38 | 98 | 133 | 44.2 | -77.05
Ontario | Dorchester | Ontario Dorchester | 260 | 0.6 | -32 | 39 | 102 | 139 | 42.98 | -81.07
Ontario | Dorion | Ontario Dorion | 200 | 0.8 | -44 | 35 | 94 | 127 | 48.78 | -88.53
Ontario | Dresden | Ontario Dresden | 185 | 0.3 | -30 | 39 | 98 | 134 | 42.58 | -82.18
Ontario | Dryden | Ontario Dryden | 370 | 0.7 | -46 | 38 | 84 | 114 | 49.78 | -92.75
Ontario | Dundalk | Ontario Dundalk | 525 | 1 | -37 | 37 | 94 | 128 | 44.17 | -80.39
Ontario | Dunnville | Ontario Dunnville | 175 | 0.6 | -31 | 38 | 102 | 139 | 42.9 | -79.62
Ontario | Durham | Ontario Durham | 340 | 0.8 | -37 | 37 | 98 | 133 | 44.17 | -80.82
Ontario | Dutton | Ontario Dutton | 225 | 0.4 | -32 | 39 | 100 | 137 | 42.67 | -81.5
Ontario | Earlton | Ontario Earlton | 245 | 0.9 | -47 | 39 | 88 | 118 | 47.72 | -79.82
Ontario | Edison | Ontario Edison | 365 | 0.7 | -46 | 38 | 85 | 115 | 49.8 | -93.55
Ontario | Elliot Lake | Ontario Elliot Lake | 380 | 0.9 | -45 | 37 | 88 | 119 | 46.38 | -82.66
Ontario | Elmvale | Ontario Elmvale | 220 | 0.8 | -36 | 38 | 89 | 121 | 44.58 | -79.87
Ontario | Embro | Ontario Embro | 310 | 0.6 | -33 | 38 | 100 | 136 | 43.15 | -80.9
Ontario | Englehart | Ontario Englehart | 205 | 0.8 | -47 | 39 | 84 | 113 | 47.82 | -79.87
Ontario | Espanola | Ontario Espanola | 220 | 0.7 | -45 | 38 | 94 | 127 | 46.25 | -81.77
Ontario | Exeter | Ontario Exeter | 265 | 0.7 | -33 | 38 | 98 | 134 | 43.35 | -81.48
Ontario | Fenelon Falls | Ontario Fenelon Falls | 260 | 0.7 | -40 | 38 | 84 | 114 | 44.53 | -78.75
Ontario | Fergus | Ontario Fergus | 400 | 0.7 | -35 | 38 | 94 | 128 | 43.7 | -80.37
Ontario | Forest | Ontario Forest | 215 | 0.6 | -32 | 39 | 98 | 134 | 43.1 | -82
Ontario | Fort Erie | Ontario Fort Erie | 180 | 0.7 | -29 | 38 | 102 | 139 | 42.9 | -78.93
Ontario | Fort Erie (Ridgeway) | Ontario Fort Erie (Ridgeway) | 190 | 0.7 | -29 | 38 | 102 | 139 | 42.8836 | -79.0574
Ontario | Fort Frances | Ontario Fort Frances | 340 | 0.7 | -46 | 38 | 84 | 114 | 48.61 | -93.39
Ontario | Gananoque | Ontario Gananoque | 80 | 0.6 | -37 | 38 | 100 | 135 | 44.33 | -76.17
Ontario | Geraldton | Ontario Geraldton | 345 | 0.9 | -49 | 38 | 85 | 114 | 49.73 | -86.95
Ontario | Glencoe | Ontario Glencoe | 215 | 0.4 | -32 | 39 | 98 | 134 | 42.75 | -81.72
Ontario | Goderich | Ontario Goderich | 185 | 0.7 | -32 | 37 | 99 | 135 | 43.75 | -81.72
Ontario | Gore Bay | Ontario Gore Bay | 205 | 0.8 | -43 | 37 | 95 | 129 | 45.92 | -82.47
Ontario | Graham | Ontario Graham | 495 | 0.8 | -47 | 28 | 84 | 114 | 49.25 | -90.57
Ontario | Gravenhurst (Muskoka Airport) | Ontario Gravenhurst (Muskoka Airport) | 255 | 0.8 | -43 | 37 | 89 | 120 | 44.9196 | -79.3742
Ontario | Grimsby | Ontario Grimsby | 85 | 0.3 | -27 | 39 | 100 | 136 | 43.2 | -79.57
Ontario | Guelph | Ontario Guelph | 340 | 0.6 | -35 | 38 | 94 | 128 | 43.55 | -80.25
Ontario | Guthrie | Ontario Guthrie | 280 | 0.7 | -39 | 38 | 86 | 117 | 44.47 | -79.55
Ontario | Haileybury | Ontario Haileybury | 210 | 0.7 | -47 | 39 | 88 | 118 | 47.45 | -79.63
Ontario | Haldimand (Caledonia) | Ontario Haldimand (Caledonia) | 190 | 0.4 | -31 | 39 | 101 | 138 | 43.0648 | -79.9551
Ontario | Haldimand (Hagersville) | Ontario Haldimand (Hagersville) | 215 | 0.4 | -31 | 39 | 101 | 138 | 42.9599 | -80.0523
Ontario | Haliburton | Ontario Haliburton | 335 | 0.9 | -42 | 38 | 80 | 108 | 45.05 | -78.52
Ontario | Halton Hills (Georgetown) | Ontario Halton Hills (Georgetown) | 255 | 0.4 | -35 | 39 | 92 | 125 | 43.6502 | -79.9036
Ontario | Hamilton | Ontario Hamilton | 90 | 0.3 | -29 | 39 | 96 | 131 | 43.25 | -79.86
Ontario | Hanover | Ontario Hanover | 270 | 0.8 | -40 | 38 | 98 | 133 | 44.15 | -81.03
Ontario | Hastings | Ontario Hastings | 200 | 0.6 | -39 | 38 | 86 | 116 | 44.3 | -77.95
Ontario | Hawkesbury | Ontario Hawkesbury | 50 | 0.7 | -41 | 37 | 96 | 129 | 45.6 | -74.62
Ontario | Hearst | Ontario Hearst | 245 | 0.8 | -39 | 38 | 80 | 107 | 49.68 | -83.67
Ontario | Honey Harbour | Ontario Honey Harbour | 180 | 0.8 | -40 | 37 | 88 | 119 | 44.87 | -79.82
Ontario | Hornepayne | Ontario Hornepayne | 360 | 1 | -50 | 37 | 80 | 107 | 49.22 | -84.78
Ontario | Huntsville | Ontario Huntsville | 335 | 0.9 | --43 | 38 | 80 | 108 | 45.33 | -79.22
Ontario | Ingersoll | Ontario Ingersoll | 280 | 0.5 | -33 | 38 | 102 | 139 | 43.03 | -80.88
Ontario | Iroquois Falls | Ontario Iroquois Falls | 275 | 0.9 | -47 | 39 | 86 | 119 | 48.77 | -80.68
Ontario | Jellicoe | Ontario Jellicoe | 330 | 0.8 | -47 | 38 | 85 | 114 | 49.68 | -87.52
Ontario | Kapuskasing | Ontario Kapuskasing | 245 | 0.9 | -47 | 38 | 85 | 11 | 49.42 | -82.43
Ontario | Kemptville | Ontario Kemptville | 90 | 0.7 | -40 | 38 | 88 | 118 | 45.02 | -75.64
Ontario | Kenora | Ontario Kenora | 370 | 0.7 | -44 | 37 | 86 | 117 | 49.82 | -94.43
Ontario | Killaloe | Ontario Killaloe | 185 | 0.8 | -44 | 38 | 80 | 108 | 45.55 | -77.42
Ontario | Kincardine | Ontario Kincardine | 190 | 0.8 | -33 | 38 | 99 | 135 | 44.18 | -81.63
Ontario | Kingston | Ontario Kingston | 80 | 0.6 | -35 | 37 | 102 | 138 | 44.23 | -76.48
Ontario | Kinmount | Ontario Kinmount | 295 | 0.8 | -40 | 38 | 80 | 108 | 44.78 | -78.65
Ontario | Kirkland Lake | Ontario Kirkland Lake | 325 | 0.9 | -47 | 39 | 86 | 115 | 48.15 | -80.03
Ontario | Kitchener | Ontario Kitchener | 335 | 0.6 | -33 | 38 | 94 | 128 | 43.45 | -80.48
Ontario | Kitchenuhmaykoosib (Big Trout Lake) | Ontario Kitchenuhmaykoosib (Big Trout Lake) | 215 | 1 | -49 | 35 | 92 | 122 | 53.7586 | -90.0764
Ontario | Lakefield | Ontario Lakefield | 240 | 0.7 | -39 | 38 | 86 | 116 | 44.43 | -78.27
Ontario | Lansdowne House | Ontario Lansdowne House | 240 | 0.9 | -49 | 37 | 85 | 113 | 52.23 | -87.88
Ontario | Leamington | Ontario Leamington | 190 | 0.2 | -29 | 39 | 98 | 134 | 42.08 | -82.57
Ontario | Lindsay | Ontario Lindsay | 265 | 0.7 | -40 | 38 | 86 | 117 | 44.35 | -78.73
Ontario | Lion’s Head | Ontario Lion’s Head | 185 | 0.8 | -35 | 37 | 96 | 130 | 44.98 | -81.25
Ontario | Listowel | Ontario Listowel | 380 | 0.8 | -35 | 37 | 97 | 132 | 43.73 | -80.95
Ontario | London | Ontario London | 245 | 0.6 | -33 | 39 | 100 | 137 | 42.98 | -81.23
Ontario | Lucan | Ontario Lucan | 300 | 0.7 | -33 | 38 | 98 | 134 | 43.18 | -81.4
Ontario | Maitland | Ontario Maitland | 85 | 0.7 | -37 | 38 | 93 | 125 | 44.63 | -75.62
Ontario | Markdale | Ontario Markdale | 425 | 1 | -37 | 37 | 96 | 130 | 44.32 | -80.65
Ontario | Markham | Ontario Markham | 175 | 0.4 | -34 | 39 | 95 | 129 | 43.87 | -79.27
Ontario | Martin | Ontario Martin | 485 | 0.8 | -47 | 38 | 84 | 114 | 49.25 | -91.13
Ontario | Matheson | Ontario Matheson | 265 | 0.8 | -47 | 39 | 86 | 115 | 48.53 | -80.47
Ontario | Mattawa | Ontario Mattawa | 165 | 0.6 | -43 | 38 | 86 | 116 | 46.32 | -78.7
Ontario | Midland | Ontario Midland | 190 | 0.8 | -40 | 38 | 90 | 122 | 44.75 | -79.88
Ontario | Milton | Ontario Milton | 200 | 0.4 | -34 | 39 | 95 | 129 | 43.52 | -79.88
Ontario | Milverton | Ontario Milverton | 370 | 0.7 | -35 | 38 | 98 | 134 | 43.57 | -80.92
Ontario | Minden | Ontario Minden | 270 | 0.8 | -41 | 38 | 80 | 108 | 44.92 | -78.73
Ontario | Mississauga | Ontario Mississauga | 160 | 0.3 | -33 | 39 | 98 | 133 | 43.58 | -79.65
Ontario | Mississauga (Lester B. Pearson Int'l Airport) | Ontario Mississauga (Lester B. Pearson Int'l Airport) | 170 | 0.3 | -33 | 39 | 99 | 135 | 43.68 | -77.58
Ontario | Mississauga (Port Credit) | Ontario Mississauga (Port Credit) | 75 | 0.3 | -31 | 39 | 99 | 135 | 43.55 | -79.58
Ontario | Mitchell | Ontario Mitchell | 335 | 0.7 | -34 | 37 | 98 | 134 | 43.47 | -81.2
Ontario | Moosonee | Ontario Moosonee | 10 | 0.8 | -49 | 38 | 88 | 117 | 51.32 | -80.72
Ontario | Morrisburg | Ontario Morrisburg | 75 | 0.7 | -40 | 38 | 93 | 125 | 44.9 | -75.18
Ontario | Mount Forest | Ontario Mount Forest | 420 | 0.8 | -37 | 38 | 96 | 131 | 43.98 | -80.73
Ontario | Nakina | Ontario Nakina | 325 | 0.8 | -49 | 38 | 80 | 107 | 50.17 | -86.7
Ontario | Nanticoke (Jarvis) | Ontario Nanticoke (Jarvis) | 205 | 0.4 | -32 | 38 | 101 | 138 | 42.8849 | -80.1107
Ontario | Nanticoke (Port Dover) | Ontario Nanticoke (Port Dover) | 180 | 0.4 | -32 | 37 | 102 | 139 | 42.7865 | -80.2033
Ontario | Napanee | Ontario Napanee | 90 | 0.6 | -38 | 38 | 98 | 133 | 44.25 | -76.95
Ontario | Newcastle | Ontario Newcastle | 115 | 0.4 | -32 | 38 | 99 | 134 | 43.92 | -78.58
Ontario | Newcastle (Bowmanville) | Ontario Newcastle (Bowmanville) | 95 | 0.4 | -32 | 38 | 98 | 133 | 43.91 | -78.68
Ontario | New Liskeard | Ontario New Liskeard | 180 | 0.8 | -47 | 39 | 88 | 118 | 47.5 | -79.67
Ontario | Newmarket | Ontario Newmarket | 185 | 0.6 | -35 | 38 | 88 | 119 | 44.05 | -79.47
Ontario | Niagara Falls | Ontario Niagara Falls | 210 | 0.5 | -28 | 38 | 100 | 136 | 43.1 | -79.07
Ontario | North Bay | Ontario North Bay | 210 | 0.7 | -43 | 38 | 84 | 113 | 46.32 | -79.47
Ontario | Norwood | Ontario Norwood | 225 | 0.6 | -39 | 38 | 86 | 116 | 44.38 | -77.98
Ontario | Oakville | Ontario Oakville | 90 | 0.3 | -31 | 39 | 99 | 135 | 43.45 | -79.68
Ontario | Orangeville | Ontario Orangeville | 430 | 0.7 | -36 | 37 | 92 | 125 | 43.92 | -80.1
Ontario | Orillia | Ontario Orillia | 230 | 0.7 | -39 | 38 | 88 | 119 | 44.62 | -79.42
Ontario | Oshawa | Ontario Oshawa | 110 | 0.4 | -32 | 38 | 98 | 133 | 43.9 | -78.85
Ontario | Ottawa (Barrhaven) | Ontario Ottawa (Barrhaven) | 98 | 0.7 | -39 | 38 | 90 | 121 | 45.28 | -75.76
Ontario | Ottawa (City Hall) | Ontario Ottawa (City Hall) | 70 | 0.7 | -39 | 38 | 90 | 121 | 45.42 | -75.69
Ontario | Ottawa (Kanata) | Ontario Ottawa (Kanata) | 98 | 0.7 | -39 | 38 | 90 | 121 | 45.31 | -75.91
Ontario | Ottawa (M-C Int'l Airport) | Ontario Ottawa (M-C Int'l Airport) | 125 | 0.7 | -35 | 38 | 90 | 121 | 45.32 | -75.67
Ontario | Ottawa (Orleans) | Ontario Ottawa (Orleans) | 70 | 0.7 | -40 | 38 | 92 | 124 | 45.48 | -75.52
Ontario | Owen Sound | Ontario Owen Sound | 215 | 0.8 | -34 | 36 | 95 | 129 | 44.57 | -80.93
Ontario | Pagwa River | Ontario Pagwa River | 185 | 0.8 | -48 | 38 | 80 | 107 | 50.02 | -85.22
Ontario | Paris | Ontario Paris | 245 | 0.4 | -33 | 38 | 100 | 136 | 43.2 | -80.38
Ontario | Parkhill | Ontario Parkhill | 205 | 0.6 | -34 | 39 | 98 | 134 | 43.15 | -81.68
Ontario | Parry Sound | Ontario Parry Sound | 215 | 0.8 | -43 | 38 | 90 | 122 | 45.35 | -80.03
Ontario | Pelham (Fonthill) | Ontario Pelham (Fonthill) | 230 | 0.6 | -29 | 38 | 101 | 138 | 43.0453 | -79.2854
Ontario | Pembroke | Ontario Pembroke | 125 | 0.7 | -43 | 39 | 89 | 120 | 45.82 | -77.12
Ontario | Penetanguishene | Ontario Penetanguishene | 220 | 0.8 | -40 | 38 | 94 | 127 | 44.78 | -79.92
Ontario | Perth | Ontario Perth | 130 | 0.7 | -38 | 38 | 88 | 119 | 44.9 | -76.25
Ontario | Petawawa | Ontario Petawawa | 135 | 0.8 | -43 | 39 | 89 | 120 | 45.9 | -77.33
Ontario | Peterborough | Ontario Peterborough | 200 | 0.6 | -39 | 38 | 88 | 119 | 44.3 | -78.32
Ontario | Petrolia | Ontario Petrolia | 195 | 0.4 | -32 | 39 | 98 | 134 | 42.87 | -82.15
Ontario | Pickering (Dunbarton) | Ontario Pickering (Dunbarton) | 85 | 0.3 | -31 | 38 | 98 | 133 | 43.8222 | -79.1169
Ontario | Picton | Ontario Picton | 95 | 0.6 | -33 | 37 | 105 | 142 | 44 | -77.13
Ontario | Plattsville | Ontario Plattsville | 300 | 0.6 | -33 | 38 | 98 | 134 | 43.3 | -80.62
Ontario | Point Alexander | Ontario Point Alexander | 150 | 0.7 | -43 | 39 | 89 | 120 | 46.13 | -77.57
Ontario | Port Burwell | Ontario Port Burwell | 195 | 0.4 | -32 | 38 | 102 | 139 | 42.65 | -80.82
Ontario | Port Colborne | Ontario Port Colborne | 180 | 0.6 | -29 | 38 | 102 | 139 | 42.9 | -79.23
Ontario | Port Elgin | Ontario Port Elgin | 205 | 0.8 | -35 | 36 | 99 | 135 | 44.43 | -81.4
Ontario | Port Hope | Ontario Port Hope | 100 | 0.4 | -32 | 38 | 99 | 134 | 43.95 | -78.3
Ontario | Port Perry | Ontario Port Perry | 270 | 0.7 | -36 | 38 | 88 | 119 | 44.1 | -78.95
Ontario | Port Stanley | Ontario Port Stanley | 180 | 0.4 | -33 | 38 | 101 | 138 | 42.67 | -81.22
Ontario | Prescott | Ontario Prescott | 90 | 0.7 | -37 | 38 | 93 | 125 | 44.72 | -75.52
Ontario | Princeton | Ontario Princeton | 280 | 0.4 | -33 | 38 | 100 | 136 | 43.17 | -80.53
Ontario | Raith | Ontario Raith | 475 | 0.8 | -49 | 38 | 82 | 111 | 48.83 | -89.93
Ontario | Rayside-Balfour (Chlemsford) | Ontario Rayside-Balfour (Chlemsford) | 270 | 0.7 | -43 | 39 | 91 | 123 | 46.5776 | -81.198
Ontario | Red Lake | Ontario Red Lake | 360 | 0.8 | -46 | 38 | 80 | 108 | 51.05 | -93.82
Ontario | Renfrew | Ontario Renfrew | 115 | 0.7 | -40 | 39 | 88 | 118 | 45.47 | -76.68
Ontario | Richmond Hill | Ontario Richmond Hill | 230 | 0.4 | -33 | 39 | 92 | 125 | 43.87 | -79.45
Ontario | Rockland | Ontario Rockland | 50 | 0.7 | -40 | 38 | 95 | 128 | 45.55 | -75.29
Ontario | Sarnia | Ontario Sarnia | 190 | 0.3 | -30 | 39 | 98 | 134 | 42.97 | -82.38
Ontario | Sault Ste. Marie | Ontario Sault Ste. Marie | 190 | 0.9 | -41 | 37 | 98 | 133 | 46.5136 | -84.3358
Ontario | Schreiber | Ontario Schreiber | 310 | 1 | -43 | 33 | 94 | 127 | 48.8 | -87.25
Ontario | Seaforth | Ontario Seaforth | 310 | 0.7 | -34 | 37 | 98 | 134 | 43.55 | -81.4
Ontario | Shelburne | Ontario Shelburne | 495 | 0.9 | -37 | 37 | 93 | 126 | 44.08 | -80.2
Ontario | Simcoe | Ontario Simcoe | 210 | 0.4 | -32 | 38 | 101 | 138 | 42.83 | -80.3
Ontario | Sioux Lookout | Ontario Sioux Lookout | 375 | 0.8 | -46 | 38 | 82 | 111 | 50.07 | -91.98
Ontario | Smiths Falls | Ontario Smiths Falls | 130 | 0.7 | -38 | 38 | 88 | 119 | 44.9 | -76.02
Ontario | Smithville | Ontario Smithville | 185 | 0.4 | -29 | 38 | 101 | 138 | 43.1 | -79.55
Ontario | Smooth Rock Falls | Ontario Smooth Rock Falls | 235 | 0.8 | -48 | 38 | 84 | 112 | 49.2753 | -81.6209
Ontario | Southampton | Ontario Southampton | 180 | 0.8 | -35 | 36 | 99 | 135 | 44.4949 | -81.3696
Ontario | South River | Ontario South River | 355 | 0.8 | -45 | 38 | 80 | 108 | 45.83 | -79.38
Ontario | St. Catharine | Ontario St. Catharine | 105 | 0.3 | -27 | 39 | 102 | 139 | 43.17 | -79.25
Ontario | St. Mary's | Ontario St. Mary's | 310 | 0.7 | -33 | 38 | 98 | 134 | 43.25 | -81.13
Ontario | St. Thomas | Ontario St. Thomas | 225 | 0.4 | -33 | 39 | 101 | 138 | 42.78 | -81.2
Ontario | Stirling | Ontario Stirling | 120 | 0.5 | -45 | 38 | 88 | 119 | 44.3 | -77.55
Ontario | Stratford | Ontario Stratford | 360 | 0.7 | -33 | 38 | 98 | 134 | 43.37 | -80.95
Ontario | Strathroy | Ontario Strathroy | 225 | 0.6 | -33 | 39 | 98 | 134 | 42.95 | -81.63
Ontario | Sturgeon Falls | Ontario Sturgeon Falls | 205 | 0.7 | -43 | 38 | 88 | 119 | 46.37 | -79.92
Ontario | Sudbury | Ontario Sudbury | 275 | 0.7 | -43 | 39 | 92 | 124 | 46.5 | -81
Ontario | Sundridge | Ontario Sundridge | 340 | 0.8 | -45 | 38 | 80 | 108 | 45.77 | -79.4
Ontario | Tavistock | Ontario Tavistock | 340 | 0.6 | -33 | 38 | 98 | 134 | 43.32 | -80.83
Ontario | Temagami | Ontario Temagami | 300 | 0.8 | -47 | 39 | 87 | 117 | 47.07 | -79.78
Ontario | Thamesford | Ontario Thamesford | 280 | 0.6 | -33 | 38 | 101 | 138 | 43.07 | -81
Ontario | Thedford | Ontario Thedford | 205 | 0.6 | -34 | 39 | 98 | 134 | 43.15 | -81.85
Ontario | Thunder Bay | Ontario Thunder Bay | 210 | 0.9 | -44 | 39 | 94 | 127 | 48.4 | -89.32
Ontario | Tillsonburg | Ontario Tillsonburg | 215 | 0.4 | -33 | 39 | 101 | 138 | 42.85 | -80.73
Ontario | Timmins | Ontario Timmins | 300 | 0.9 | -48 | 39 | 85 | 114 | 48.47 | -81.33
Ontario | Timmins (Porcupine) | Ontario Timmins (Porcupine) | 295 | 0.9 | -48 | 39 | 85 | 114 | 48.495 | -81.191
Toronto Area | Etobicoke | Toronto Area Etobicoke | 160 | 0.3 | -33 | 39 | 98 | 133 | 43.6205 | -79.5132
Toronto Area | North York | Toronto Area North York | 175 | 0.4 | -32 | 39 | 97 | 132 | 43.7615 | -79.4111
Toronto Area | Scarborough | Toronto Area Scarborough | 180 | 0.4 | -31 | 39 | 96 | 130 | 43.7764 | -79.2318
Toronto Area | Toronto (City Hall) | Toronto Area Toronto (City Hall) | 90 | 0.3 | -29 | 39 | 99 | 135 | 43.65 | -79.61
Toronto Area | Trenton | Toronto Area Trenton | 80 | 0.5 | -35 | 38 | 101 | 137 | 44.1011 | -77.5763
Toronto Area | Trout Creek | Toronto Area Trout Creek | 330 | 0.8 | -44 | 38 | 80 | 108 | 45.9869 | -79.3596
Toronto Area | Uxbridge | Toronto Area Uxbridge | 275 | 0.7 | -36 | 39 | 88 | 119 | 44.1094 | -79.1205
Toronto Area | Vaughan (Woodbridge) | Toronto Area Vaughan (Woodbridge) | 165 | 0.3 | -33 | 39 | 96 | 130 | 43.7762 | -79.6092
Toronto Area | Vittoria | Toronto Area Vittoria | 215 | 0.4 | -32 | 38 | 102 | 139 | 42.7624 | -80.323
Toronto Area | Walkerton | Toronto Area Walkerton | 275 | 0.8 | -40 | 38 | 98 | 133 | 44.1313 | -81.1507
Toronto Area | Wallaceburg | Toronto Area Wallaceburg | 180 | 0.3 | -30 | 39 | 98 | 134 | 42.5926 | -82.3882
Toronto Area | Waterloo | Toronto Area Waterloo | 330 | 0.6 | -33 | 38 | 94 | 128 | 43.4643 | -80.5204
Toronto Area | Watford | Toronto Area Watford | 240 | 0.6 | -32 | 39 | 98 | 134 | 42.9556 | -81.8799
Toronto Area | Wawa | Toronto Area Wawa | 290 | 1 | -46 | 35 | 94 | 127 | 47.9924 | -84.7711
Toronto Area | Welland | Toronto Area Welland | 180 | 0.6 | -29 | 38 | 101 | 138 | 42.9922 | -79.2483
Toronto Area | West Lorne | Toronto Area West Lorne | 215 | 0.4 | -32 | 39 | 99 | 135 | 42.6038 | -81.6067
Toronto Area | Whitby | Toronto Area Whitby | 85 | 0.4 | -31 | 38 | 99 | 134 | 43.8975 | -78.9429
Toronto Area | Whitby (Brooklin) | Toronto Area Whitby (Brooklin) | 160 | 0.6 | -33 | 38 | 95 | 129 | 43.9632 | -78.9571
Toronto Area | White River | Toronto Area White River | 375 | 1.1 | -49 | 38 | 83 | 112 | 48.594 | -85.2748
Toronto Area | Wiarton | Toronto Area Wiarton | 185 | 0.8 | -35 | 36 | 96 | 130 | 44.742 | -81.1408
Toronto Area | Windsor | Toronto Area Windsor | 185 | 0.2 | -29 | 40 | 97 | 133 | 42.3149 | -83.0364
Toronto Area | Wingham | Toronto Area Wingham | 310 | 0.8 | -36 | 38 | 98 | 133 | 43.8879 | -81.3117
Toronto Area | Woodstock | Toronto Area Woodstock | 300 | 0.6 | -33 | 38 | 100 | 136 | 43.1315 | -80.7472
Toronto Area | Wyoming | Toronto Area Wyoming | 215 | 0.5 | -32 | 39 | 97 | 133 | 42.9489 | -82.1186
Québec | Acton-Vale | Québec Acton-Vale | 95 | 0.7 | -41 | 36 | 89 | 119 | 45.65 | -72.57
Québec | Alma | Québec Alma | 110 | 1 | -43 | 37 | 92 | 122 | 48.55 | -71.65
Québec | Amos | Québec Amos | 295 | 1 | -50 | 37 | 85 | 113 | 48.57 | -78.12
Québec | Asbestos | Québec Asbestos | 245 | 0.8 | -41 | 36 | 85 | 114 | 45.77 | -71.93
Québec | Aylmer | Québec Aylmer | 90 | 0.7 | -40 | 38 | 92 | 124 | 45.4 | -75.83
Québec | Baie-Comeau | Québec Baie-Comeau | 60 | 1.3 | -42 | 34 | 101 | 133 | 49.22 | -68.15
Québec | Baie-Saint-Paul | Québec Baie-Saint-Paul | 20 | 1 | -37 | 36 | 97 | 129 | 47.44 | -70.51
Québec | Beauport | Québec Beauport | 45 | 1 | -40 | 36 | 97 | 129 | 46.87 | -71.18
Québec | Bedford | Québec Bedford | 55 | 0.6 | -38 | 37 | 84 | 113 | 45.12 | -72.98
Québec | Beloeil | Québec Beloeil | 25 | 0.7 | -39 | 37 | 93 | 125 | 45.57 | -73.2
Québec | Brome | Québec Brome | 210 | 0.7 | -40 | 36 | 83 | 111 | 45.2 | -72.57
Québec | Brossard | Québec Brossard | 15 | 0.7 | -37 | 37 | 100 | 134 | 45.45 | -73.47
Québec | Buckingham | Québec Buckingham | 130 | 0.8 | -41 | 38 | 90 | 121 | 45.58 | -75.42
Québec | Campbell's Bay | Québec Campbell's Bay | 115 | 0.8 | -41 | 38 | 85 | 114 | 45.73 | -76.6
Québec | Cap-aux-Meules | Québec Cap-aux-Meules | 8 | 1.1 | -28 | 31 | 110 | 144 | 47.3777 | -61.8714
Québec | Chambly | Québec Chambly | 20 | 0.7 | -38 | 37 | 94 | 126 | 45.45 | -73.28
Québec | Coaticook | Québec Coaticook | 295 | 0.7 | -40 | 35 | 80 | 107 | 45.13 | -71.8
Québec | Contrecoeur | Québec Contrecoeur | 10 | 0.8 | -40 | 37 | 96 | 128 | 45.85 | -73.23
Québec | Cowansville | Québec Cowansville | 120 | 0.7 | -38 | 36 | 83 | 111 | 45.2 | -72.75
Québec | Deux-Montagnes | Québec Deux-Montagnes | 25 | 0.7 | -39 | 37 | 91 | 122 | 45.53 | -73.88
Québec | Dolbeau | Québec Dolbeau | 120 | 1 | -49 | 37 | 89 | 118 | 48.88 | -72.23
Québec | Drummondville | Québec Drummondville | 85 | 0.7 | -41 | 37 | 89 | 119 | 45.88 | -72.48
Québec | Farnham | Québec Farnham | 60 | 0.7 | -38 | 36 | 87 | 117 | 45.28 | -72.98
Québec | Fort-Coulonge | Québec Fort-Coulonge | 110 | 0.7 | -42 | 38 | 85 | 114 | 45.85 | -76.73
Québec | Gagnon | Québec Gagnon | 545 | 1.4 | -49 | 34 | 85 | 111 | 51.93 | -68.17
Québec | Gaspé | Québec Gaspé | 55 | 1.3 | -35 | 36 | 96 | 126 | 48.83 | -64.48
Québec | Gatineau | Québec Gatineau | 95 | 0.7 | -40 | 38 | 96 | 129 | 45.5 | -75.65
Québec | Gracefield | Québec Gracefield | 175 | 0.8 | -45 | 38 | 85 | 114 | 46.1 | -76.05
Québec | Granby | Québec Granby | 120 | 0.7 | -38 | 36 | 86 | 115 | 45.4 | -72.73
Québec | Harrington-Harbour | Québec Harrington-Harbour | 30 | 1.5 | -39 | 30 | 127 | 164 | 50.5 | -59.48
Québec | Havre-St-Pierre | Québec Havre-St-Pierre | 5 | 1.2 | -40 | 31 | 115 | 150 | 50.23 | -63.6
Québec | Hemmingford | Québec Hemmingford | 75 | 0.7 | -40 | 38 | 90 | 121 | 45.05 | -73.58
Québec | Hull | Québec Hull | 65 | 0.7 | -40 | 38 | 96 | 129 | 45.43 | -75.73
Québec | Iberville | Québec Iberville | 35 | 0.7 | -38 | 37 | 90 | 121 | 45.35 | -73.23
Québec | Inukjuak | Québec Inukjuak | 5 | 0.8 | -47 | 30 | 100 | 129 | 58.48 | -78.1
Québec | Joliette | Québec Joliette | 45 | 0.9 | -40 | 38 | 86 | 115 | 46.02 | -73.45
Québec | Kuujjuaq | Québec Kuujjuaq | 25 | 1 | -47 | 34 | 116 | 147 | 58.1 | -68.4
Québec | Kuujjuarapik | Québec Kuujjuarapik | 20 | 0.9 | -48 | 36 | 100 | 130 | 55.28 | -77.75
Québec | Lachute | Québec Lachute | 65 | 0.7 | -41 | 37 | 88 | 118 | 45.65 | -74.33
Québec | Lac-Mégantic | Québec Lac-Mégantic | 420 | 1 | -40 | 36 | 80 | 107 | 45.58 | -70.88
Québec | La-Malbaie | Québec La-Malbaie | 25 | 0.9 | -39 | 36 | 102 | 135 | 47.65 | -70.15
Québec | La Pocatiére | Québec La Pocatiére | 55 | 1 | -37 | 36 | 105 | 139 | 47.37 | -70.04
Québec | La-Tuque | Québec La-Tuque | 165 | 1 | -44 | 38 | 80 | 106 | 47.43 | -72.78
Québec | Lennoxville | Québec Lennoxville | 155 | 0.6 | -42 | 36 | 85 | 114 | 45.37 | -71.85
Québec | Léry | Québec Léry | 30 | 0.7 | -37 | 36 | 97 | 130 | 45.35 | -73.8
Québec | Loretteville | Québec Loretteville | 100 | 1.1 | -40 | 36 | 95 | 126 | 46.85 | -71.35
Québec | Louiseville | Québec Louiseville | 15 | 0.9 | -41 | 37 | 90 | 120 | 46.25 | -72.95
Québec | Magog | Québec Magog | 215 | 0.7 | -39 | 35 | 88 | 118 | 45.27 | -72.13
Québec | Malartic | Québec Malartic | 325 | 1 | -46 | 37 | 85 | 114 | 48.13 | -78.13
Québec | Maniwaki | Québec Maniwaki | 180 | 0.7 | -45 | 38 | 85 | 114 | 46.38 | -75.97
Québec | Masson | Québec Masson | 5 | 0.7 | -41 | 38 | 95 | 128 | 45.53 | -75.42
Québec | Matane | Québec Matane | 50 | 1.1 | -36 | 34 | 106 | 139 | 48.85 | -67.53
Québec | Mont-Joli | Québec Mont-Joli | 90 | 1.2 | -35 | 36 | 104 | 137 | 48.58 | -68.18
Québec | Mont-Laurier | Québec Mont-Laurier | 225 | 0.8 | -48 | 37 | 82 | 110 | 46.55 | -75.5
Québec | Montmagny | Québec Montmagny | 10 | 0.9 | -38 | 36 | 101 | 134 | 46.98 | -70.55
Montréal Area | Beaconsfield | Montréal Area Beaconsfield | 25 | 0.7 | -38 | 37 | 98 | 131 | 45.43 | -73.87
Montréal Area | Dorval | Montréal Area Dorval | 25 | 0.7 | -37 | 37 | 101 | 135 | 45.45 | -73.75
Montréal Area | Laval | Montréal Area Laval | 35 | 0.8 | -37 | 37 | 95 | 127 | 45.58 | -73.75
Montréal Area | Montréal (City Hall) | Montréal Area Montréal (City Hall) | 20 | 0.8 | -36 | 37 | 98 | 131 | 45.51 | -73.55
Montréal Area | Montréal-Est | Montréal Area Montréal-Est | 25 | 0.8 | -38 | 37 | 98 | 131 | 45.63 | -73.52
Montréal Area | Montréal-Nord | Montréal Area Montréal-Nord | 20 | 0.8 | -37 | 37 | 98 | 131 | 45.6 | -73.63
Montréal Area | Outremont | Montréal Area Outremont | 105 | 0.8 | -36 | 37 | 98 | 131 | 45.52 | -73.62
Montréal Area | Pierrefonds | Montréal Area Pierrefonds | 25 | 0.7 | -38 | 37 | 97 | 130 | 45.48 | -73.87
Montréal Area | St-Lambert | Montréal Area St-Lambert | 15 | 0.7 | -37 | 37 | 101 | 135 | 45.5 | -73.5
Montréal Area | St-Laurent | Montréal Area St-Laurent | 45 | 0.7 | -36 | 37 | 98 | 131 | 45.5 | -73.67
Montréal Area | Ste-Anne-de-Bellevue | Montréal Area Ste-Anne-de-Bellevue | 35 | 0.7 | -38 | 37 | 96 | 129 | 45.42 | -73.93
Montréal Area | Verdun | Montréal Area Verdun | 20 | 0.7 | -36 | 37 | 101 | 135 | 45.45 | -73.57
Montréal Area | Nicolet (Gentilly) | Montréal Area Nicolet (Gentilly) | 15 | 0.8 | -41 | 37 | 96 | 128 | 46.4 | -72.28
Montréal Area | Nitchequon | Montréal Area Nitchequon | 545 | 1 | -51 | 33 | 96 | 125 | 53.21 | -70.91
Montréal Area | Noranda | Montréal Area Noranda | 305 | 1 | -45 | 37 | 85 | 114 | 48.25 | -79.02
Montréal Area | Percé | Montréal Area Percé | 5 | 1.1 | -35 | 34 | 110 | 144 | 48.53 | -64.22
Montréal Area | Pincourt | Montréal Area Pincourt | 25 | 0.7 | -39 | 37 | 96 | 129 | 45.38 | -73.98
Montréal Area | Plessisville | Montréal Area Plessisville | 145 | 0.8 | -41 | 35 | 87 | 116 | 46.22 | -71.78
Montréal Area | Port-Cartier | Montréal Area Port-Cartier | 20 | 1.2 | -43 | 34 | 107 | 140 | 50.02 | -66.87
Montréal Area | Puvinrituq | Montréal Area Puvinrituq | 5 | 0.9 | -48 | 29 | 108 | 138 | 60.03 | -77.28
Québec and environs | Ancienne-Lorette | Québec and environs Ancienne-Lorette | 35 | 1 | -38 | 36 | 96 | 128 | 46.78 | -71.38
Québec and environs | Lévis | Québec and environs Lévis | 50 | 1 | -38 | 36 | 96 | 128 | 46.8 | -71.18
Québec and environs | Québec | Québec and environs Québec | 120 | 1.1 | -38 | 36 | 96 | 128 | 46.8 | -71.23
Québec and environs | Sillery | Québec and environs Sillery | 10 | 0.9 | -38 | 36 | 96 | 128 | 46.77 | -71.25
Québec and environs | Ste-Foy | Québec and environs Ste-Foy | 115 | 1.1 | -38 | 36 | 96 | 128 | 46.78 | -71.28
Québec | Richmond | Québec Richmond | 150 | 0.7 | -41 | 36 | 85 | 114 | 45.67 | -72.15
Québec | Rimouski | Québec Rimouski | 30 | 1.1 | -35 | 36 | 102 | 134 | 48.43 | -68.55
Québec | Riviére-du-Loup | Québec Riviére-du-Loup | 55 | 1 | -37 | 35 | 104 | 138 | 47.83 | -69.53
Québec | Roberval | Québec Roberval | 100 | 1 | -45 | 38 | 90 | 119 | 48.52 | -72.23
Québec | Rock-Island | Québec Rock-Island | 160 | 0.6 | -39 | 35 | 80 | 107 | 45.04 | -72.1
Québec | Rosemére | Québec Rosemére | 25 | 0.8 | -41 | 37 | 95 | 127 | 45.63 | -73.8
Québec | Rouyn | Québec Rouyn | 300 | 0.9 | -45 | 37 | 87 | 116 | 48.23 | -79.02
Québec | Saguenay | Québec Saguenay | 10 | 0.8 | -42 | 38 | 90 | 119 | 48.43 | -71.07
Québec | Saguenay (Bagotville) | Québec Saguenay (Bagotville) | 5 | 0.8 | -42 | 38 | 92 | 122 | 48.35 | -70.88
Québec | Saguenay (Jonquière) | Québec Saguenay (Jonquière) | 135 | 0.9 | -42 | 38 | 90 | 119 | 48.42 | -71.22
Québec | Saguenay (Kénogami) | Québec Saguenay (Kénogami) | 140 | 0.9 | -42 | 38 | 90 | 119 | 48.42 | -71.25
Québec | Saint-Eustache | Québec Saint-Eustache | 35 | 0.7 | -40 | 37 | 91 | 122 | 45.56 | -73.9
Québec | Saint-Jean-sur-Richelieu | Québec Saint-Jean-sur-Richelieu | 35 | 0.7 | -38 | 37 | 90 | 121 | 45.31 | -73.26
Québec | Salaberry-de-Valleyfield | Québec Salaberry-de-Valleyfield | 50 | 0.7 | -39 | 37 | 95 | 128 | 45.25 | -74.13
Québec | Schefferville | Québec Schefferville | 550 | 1.3 | -50 | 33 | 103 | 132 | 54.8 | -66.83
Québec | Senneterre | Québec Senneterre | 310 | 1 | -50 | 37 | 80 | 107 | 48.38 | -77.23
Québec | Sept-Îles | Québec Sept-Îles | 5 | 1.2 | -42 | 34 | 110 | 144 | 50.2 | -66.38
Québec | Shawinigan | Québec Shawinigan | 60 | 0.9 | -41 | 38 | 84 | 112 | 46.55 | -72.75
Québec | Shawville | Québec Shawville | 170 | 0.8 | -41 | 38 | 87 | 117 | 45.6 | -76.48
Québec | Sherbrooke | Québec Sherbrooke | 185 | 0.7 | -41 | 36 | 85 | 114 | 45.42 | -71.9
Québec | Sorel | Québec Sorel | 10 | 0.8 | -42 | 37 | 96 | 128 | 46.03 | -73.12
Québec | St-Félicien | Québec St-Félicien | 105 | 1 | -47 | 38 | 90 | 119 | 48.65 | -72.45
Québec | St-Georges-de-Cacouna | Québec St-Georges-de-Cacouna | 35 | 1 | -37 | 35 | 104 | 137 | 47.92 | -69.5
Québec | St-Hubert | Québec St-Hubert | 25 | 0.7 | -37 | 37 | 101 | 135 | 45.5 | -73.42
Québec | St-Hubert-de-Riviére-du-Loup | Québec St-Hubert-de-Riviére-du-Loup | 310 | 1.3 | -39 | 35 | 80 | 106 | 47.82 | -69.15
Québec | St-Hyacinthe | Québec St-Hyacinthe | 35 | 0.7 | -40 | 37 | 89 | 119 | 45.62 | -72.95
Québec | St-Jérôme | Québec St-Jérôme | 95 | 0.8 | -41 | 37 | 87 | 117 | 45.78 | -74
Québec | St-Jovite | Québec St-Jovite | 230 | 0.8 | -42 | 37 | 82 | 110 | 46.12 | -74.6
Québec | St-Lazare-Hudson | Québec St-Lazare-Hudson | 60 | 0.7 | -39 | 37 | 95 | 127 | 45.4 | -74.14
Québec | St-Nicolas | Québec St-Nicolas | 65 | 1 | -40 | 36 | 97 | 129 | 46.7 | -71.4
Québec | Ste-Agathe-des-Monts | Québec Ste-Agathe-des-Monts | 360 | 1 | -41 | 37 | 89 | 119 | 46.05 | -74.28
Québec | Sutton | Québec Sutton | 185 | 0.7 | -39 | 36 | 80 | 107 | 45.1 | -72.62
Québec | Tadoussac | Québec Tadoussac | 65 | 1.1 | -37 | 35 | 108 | 143 | 48.15 | -69.72
Québec | Témiscaming | Québec Témiscaming | 240 | 0.7 | -43 | 39 | 83 | 112 | 46.72 | -79.1
Québec | Terrebonne | Québec Terrebonne | 20 | 0.8 | -40 | 37 | 95 | 127 | 45.69 | -73.63
Québec | Thetford Mines | Québec Thetford Mines | 330 | 1 | -40 | 35 | 84 | 112 | 46.08 | -71.3
Québec | Thurso | Québec Thurso | 50 | 0.7 | -41 | 38 | 95 | 128 | 45.6 | -75.25
Québec | Trois–Rivières | Québec Trois–Rivières | 25 | 0.8 | -38 | 37 | 96 | 128 | 46.35 | -72.55
Québec | Val-d'Or | Québec Val-d'Or | 310 | 1 | -46 | 37 | 85 | 113 | 48.1 | -77.78
Québec | Varennes | Québec Varennes | 15 | 0.8 | -37 | 37 | 95 | 127 | 45.68 | -73.43
Québec | Verchères | Québec Verchères | 15 | 0.8 | -39 | 37 | 98 | 131 | 45.78 | -73.35
Québec | Victoriaville | Québec Victoriaville | 125 | 0.8 | -40 | 35 | 86 | 115 | 46.05 | -71.97
Québec | Ville-Marie | Québec Ville-Marie | 200 | 0.7 | -47 | 39 | 88 | 118 | 47.33 | -79.43
Québec | Wakefield | Québec Wakefield | 120 | 0.7 | -42 | 38 | 86 | 116 | 45.64 | -75.93
Québec | Waterloo | Québec Waterloo | 205 | 0.7 | -41 | 36 | 86 | 115 | 45.35 | -72.52
Québec | Windsor | Québec Windsor | 150 | 0.7 | -41 | 36 | 85 | 114 | 45.57 | -72
New Brunswick | Alma | New Brunswick Alma | 5 | 0.8 | -32 | 34 | 102 | 135 | 45.6 | -64.95
New Brunswick | Bathurst | New Brunswick Bathurst | 10 | 1.2 | -38 | 38 | 100 | 132 | 47.6 | -65.65
New Brunswick | Boiestown | New Brunswick Boiestown | 65 | 1 | -40 | 38 | 94 | 124 | 46.4557 | -66.4197
New Brunswick | Campbellton | New Brunswick Campbellton | 30 | 1.3 | -38 | 38 | 95 | 125 | 48 | -66.67
New Brunswick | Edmundston | New Brunswick Edmundston | 160 | 1 | -40 | 37 | 80 | 106 | 47.37 | -68.33
New Brunswick | Fredericton | New Brunswick Fredericton | 15 | 0.9 | -39 | 37 | 93 | 123 | 45.95 | -66.65
New Brunswick | Gagetown | New Brunswick Gagetown | 20 | 0.8 | -38 | 37 | 95 | 126 | 45.79 | -66.16
New Brunswick | Grand Falls | New Brunswick Grand Falls | 115 | 1.1 | -40 | 36 | 90 | 119 | 47.05 | -67.73
New Brunswick | Miramichi | New Brunswick Miramichi | 5 | 1 | -37 | 38 | 98 | 129 | 47.03 | -65.47
New Brunswick | Moncton | New Brunswick Moncton | 20 | 0.9 | -37 | 37 | 105 | 139 | 46.1 | -64.78
New Brunswick | Oromocto | New Brunswick Oromocto | 20 | 0.9 | -37 | 37 | 94 | 125 | 45.84 | -66.48
New Brunswick | Sackville | New Brunswick Sackville | 15 | 0.7 | -34 | 35 | 102 | 135 | 45.88 | -64.37
New Brunswick | Saint Andrews | New Brunswick Saint Andrews | 35 | 0.8 | -32 | 36 | 96 | 128 | 45.07 | -67.05
New Brunswick | Saint George | New Brunswick Saint George | 35 | 0.8 | -35 | 37 | 96 | 128 | 45.13 | -66.82
New Brunswick | Saint John | New Brunswick Saint John | 5 | 0.7 | -31 | 35 | 100 | 133 | 45.27 | -66.05
New Brunswick | Shippagan | New Brunswick Shippagan | 5 | 1 | -32 | 36 | 114 | 150 | 47.73 | -64.7
New Brunswick | St. Stephen | New Brunswick St. Stephen | 20 | 0.9 | -35 | 37 | 87 | 116 | 45.2 | -67.28
New Brunswick | Woodstock | New Brunswick Woodstock | 60 | 0.9 | -43 | 38 | 87 | 115 | 46.16 | -67.6
Nova Scotia | Amherst | Nova Scotia Amherst | 25 | 0.7 | -36 | 35 | 102 | 135 | 45.83 | -64.2
Nova Scotia | Antigonish | Nova Scotia Antigonish | 10 | 0.7 | -36 | 37 | 104 | 137 | 45.62 | -62
Nova Scotia | Bridgewater | Nova Scotia Bridgewater | 10 | 0.6 | -30 | 35 | 105 | 140 | 44.38 | -64.52
Nova Scotia | Canso | Nova Scotia Canso | 5 | 0.5 | -28 | 32 | 112 | 148 | 45.33 | -61
Nova Scotia | Debert | Nova Scotia Debert | 45 | 0.6 | -37 | 36 | 104 | 138 | 45.43 | -63.47
Nova Scotia | Digby | Nova Scotia Digby | 35 | 0.7 | -25 | 33 | 106 | 141 | 44.62 | -65.77
Nova Scotia | Greenwood (CFB) | Nova Scotia Greenwood (CFB) | 28 | 0.8 | -32 | 36 | 110 | 146 | 44.98 | -64.9
Nova Scotia | Dartmouth | Nova Scotia Dartmouth | 10 | 0.5 | -29 | 36 | 110 | 146 | 44.67 | -63.57
Nova Scotia | Halifax | Nova Scotia Halifax | 55 | 0.5 | -28 | 36 | 110 | 146 | 44.65 | -63.6
Nova Scotia | Kentville | Nova Scotia Kentville | 25 | 0.8 | -32 | 37 | 98 | 130 | 45.08 | -64.5
Nova Scotia | Liverpool | Nova Scotia Liverpool | 20 | 0.5 | -29 | 37 | 109 | 145 | 44.03 | -64.72
Nova Scotia | Lockeport | Nova Scotia Lockeport | 5 | 0.4 | -27 | 35 | 116 | 155 | 43.7 | -65.12
Nova Scotia | Louisbourg | Nova Scotia Louisbourg | 5 | 0.6 | -28 | 34 | 115 | 151 | 45.92 | -59.98
Nova Scotia | Lunenburg | Nova Scotia Lunenburg | 25 | 0.6 | -28 | 37 | 108 | 144 | 44.38 | -64.32
Nova Scotia | New Glasgow | Nova Scotia New Glasgow | 30 | 0.7 | -38 | 36 | 102 | 135 | 45.58 | -62.65
Nova Scotia | North Sydney | Nova Scotia North Sydney | 20 | 0.7 | -30 | 35 | 105 | 138 | 46.22 | -60.25
Nova Scotia | Pictou | Nova Scotia Pictou | 25 | 0.7 | -33 | 36 | 104 | 137 | 45.68 | -62.72
Nova Scotia | Port Hawkesbury | Nova Scotia Port Hawkesbury | 40 | 0.6 | -29 | 36 | 108 | 142 | 45.62 | -61.35
Nova Scotia | Springhill | Nova Scotia Springhill | 185 | 0.9 | -37 | 36 | 102 | 135 | 45.65 | -64.05
Nova Scotia | Stewiacke | Nova Scotia Stewiacke | 25 | 0.5 | -36 | 36 | 98 | 130 | 45.13 | -63.35
Nova Scotia | Sydney | Nova Scotia Sydney | 5 | 0.7 | -30 | 35 | 105 | 138 | 46.15 | -60.18
Nova Scotia | Tatamagouche | Nova Scotia Tatamagouche | 25 | 0.7 | -35 | 37 | 105 | 139 | 45.72 | -63.3
Nova Scotia | Truro | Nova Scotia Truro | 25 | 0.6 | -36 | 36 | 102 | 135 | 45.37 | -63.27
Nova Scotia | Wolfville | Nova Scotia Wolfville | 35 | 0.8 | -29 | 37 | 98 | 130 | 45.08 | -64.37
Nova Scotia | Yarmouth | Nova Scotia Yarmouth | 10 | 0.5 | -23 | 31 | 112 | 150 | 43.83 | -66.12
Prince Edward Island | Charlottetown | Prince Edward Island Charlottetown | 5 | 0.8 | -31 | 35 | 108 | 142 | 46.23 | -63.13
Prince Edward Island | Souris | Prince Edward Island Souris | 5 | 0.8 | -28 | 35 | 114 | 150 | 46.35 | -62.25
Prince Edward Island | Summerside | Prince Edward Island Summerside | 10 | 0.9 | -31 | 35 | 109 | 144 | 46.4 | -63.78
Prince Edward Island | Tignish | Prince Edward Island Tignish | 10 | 1 | -32 | 36 | 118 | 155 | 46.95 | -64.03
Newfoundland and Labrador | Argentia | Newfoundland and Labrador Argentia | 15 | 0.7 | -24 | 28 | 125 | 162 | 47.3 | -53.98
Newfoundland and Labrador | Bonavista | Newfoundland and Labrador Bonavista | 15 | 0.9 | -27 | 31 | 140 | 181 | 48.65 | -53.12
Newfoundland and Labrador | Buchans | Newfoundland and Labrador Buchans | 255 | 1.4 | -34 | 34 | 100 | 130 | 48.82 | -56.87
Newfoundland and Labrador | Cape Harrison | Newfoundland and Labrador Cape Harrison | 5 | 1.9 | -37 | 35 | 125 | 159 | 54.78 | -57.95
Newfoundland and Labrador | Cape Race | Newfoundland and Labrador Cape Race | 5 | 0.7 | -25 | 29 | 140 | 182 | 46.65 | -53.07
Newfoundland and Labrador | Channel-Port aux Basques | Newfoundland and Labrador Channel-Port aux Basques | 5 | 1.1 | -28 | 32 | 133 | 174 | 47.57 | -59.15
Newfoundland and Labrador | Corner Brook | Newfoundland and Labrador Corner Brook | 35 | 1.1 | -31 | 34 | 102 | 132 | 48.95 | -57.95
Newfoundland and Labrador | Gander | Newfoundland and Labrador Gander | 125 | 1.1 | -30 | 35 | 120 | 155 | 48.98 | -54.59
Newfoundland and Labrador | Grand Bank | Newfoundland and Labrador Grand Bank | 5 | 0.7 | -26 | 29 | 130 | 169 | 47.1 | -55.77
Newfoundland and Labrador | Grand Falls | Newfoundland and Labrador Grand Falls | 60 | 1 | -36 | 37 | 100 | 129 | 48.93 | -55.67
Newfoundland and Labrador | Happy Valley-Goose Bay | Newfoundland and Labrador Happy Valley-Goose Bay | 15 | 1.6 | -40 | 38 | 100 | 128 | 53.32 | -60.37
Newfoundland and Labrador | Labrador City | Newfoundland and Labrador Labrador City | 550 | 1.4 | -48 | 34 | 92 | 119 | 52.95 | -66.92
Newfoundland and Labrador | St. Anthony | Newfoundland and Labrador St. Anthony | 10 | 1.8 | -34 | 30 | 125 | 160 | 51.37 | -55.58
Newfoundland and Labrador | St. John’s | Newfoundland and Labrador St. John’s | 65 | 0.9 | -27 | 34 | 128 | 166 | 47.57 | -52.72
Newfoundland and Labrador | Stephenville | Newfoundland and Labrador Stephenville | 25 | 1.2 | -30 | 32 | 114 | 148 | 48.55 | -58.58
Newfoundland and Labrador | Twin Falls | Newfoundland and Labrador Twin Falls | 425 | 1.4 | -46 | 34 | 95 | 122 | 53.5 | -64.53
Newfoundland and Labrador | Wabana | Newfoundland and Labrador Wabana | 75 | 0.9 | -27 | 31 | 125 | 162 | 47.63 | -52.95
Newfoundland and Labrador | Wabush | Newfoundland and Labrador Wabush | 550 | 1.4 | -48 | 34 | 92 | 119 | 52.92 | -66.87
Yukon | Aishihik | Yukon Aishihik | 920 | 0.4 | -58 | 32 | 93 | 128 | 61.6 | -137.52
Yukon | Dawson | Yukon Dawson | 330 | 0.7 | -58 | 36 | 80 | 109 | 64.07 | -139.42
Yukon | Destruction Bay | Yukon Destruction Bay | 815 | 0.4 | -58 | 32 | 116 | 160 | 61.25 | -138.8
Yukon | Faro | Yukon Faro | 670 | 0.5 | -56 | 35 | 80 | 109 | 62.23 | -133.36
Yukon | Haines Junction | Yukon Haines Junction | 600 | 0.5 | -58 | 33 | 90 | 124 | 60.78 | -137.54
Yukon | Snag | Yukon Snag | 595 | 0.5 | -62 | 33 | 80 | 110 | 62.4 | -140.37
Yukon | Teslin | Yukon Teslin | 690 | 0.7 | -60 | 33 | 80 | 110 | 60.17 | -132.72
Yukon | Watson Lake | Yukon Watson Lake | 685 | 0.8 | -60 | 35 | 80 | 109 | 60.13 | -128.71
Yukon | Whitehorse | Yukon Whitehorse | 655 | 0.5 | -56 | 35 | 88 | 121 | 60.72 | -135.05
Northwest Territories | Aklavik | Northwest Territories Aklavik | 5 | 0.6 | -53 | 33 | 94 | 126 | 68.23 | -135.01
Northwest Territories | Echo Bay/Port Radium | Northwest Territories Echo Bay/Port Radium | 195 | 0.9 | -50 | 32 | 94 | 124 | 66.05 | -117.88
Northwest Territories | Fort Good Hope | Northwest Territories Fort Good Hope | 100 | 0.9 | -56 | 36 | 89 | 119 | 66.29 | -128.63
Northwest Territories | Fort McPherson | Northwest Territories Fort McPherson | 25 | 0.7 | -56 | 33 | 88 | 118 | 67.43 | -134.88
Northwest Territories | Fort Providence | Northwest Territories Fort Providence | 150 | 0.7 | -52 | 37 | 89 | 119 | 61.35 | -117.65
Northwest Territories | Fort Resolution | Northwest Territories Fort Resolution | 160 | 0.7 | -51 | 35 | 88 | 117 | 61.19 | -113.67
Northwest Territories | Fort Simpson | Northwest Territories Fort Simpson | 120 | 0.7 | -54 | 37 | 89 | 120 | 61.93 | -121.35
Northwest Territories | Fort Smith | Northwest Territories Fort Smith | 205 | 0.7 | -53 | 37 | 80 | 107 | 60 | -111.88
Northwest Territories | Hay River | Northwest Territories Hay River | 45 | 0.7 | -51 | 37 | 84 | 113 | 60.85 | -115.73
Northwest Territories | Inuvik | Northwest Territories Inuvik | 45 | 0.6 | -56 | 34 | 91 | 122 | 68.35 | -133.72
Northwest Territories | Mould Bay | Northwest Territories Mould Bay | 5 | 0.3 | -55 | 19 | 100 | 127 | 76.23 | -119.33
Northwest Territories | Norman Wells | Northwest Territories Norman Wells | 65 | 0.9 | -53 | 35 | 88 | 118 | 65.28 | -126.85
Northwest Territories | Rae-Edzo | Northwest Territories Rae-Edzo | 160 | 0.7 | -53 | 35 | 89 | 118 | 62.83 | -116.05
Northwest Territories | Tungsten | Northwest Territories Tungsten | 1340 | 1.3 | -55 | 32 | 90 | 122 | 61.95 | -128.27
Northwest Territories | Ulukhaqtuuq/Holman | Northwest Territories Ulukhaqtuuq/Holman | 10 | 0.4 | -50 | 29 | 107 | 139 | 70.73 | -117.75
Northwest Territories | Wrigley | Northwest Territories Wrigley | 80 | 0.8 | -54 | 36 | 88 | 118 | 63.23 | -123.47
Northwest Territories | Yellowknife | Northwest Territories Yellowknife | 160 | 0.7 | -51 | 33 | 86 | 114 | 62.48 | -114.35
Nunavut | Alert | Nunavut Alert | 5 | 0.5 | -51 | 21 | 125 | 143 | 82.48 | -62.25
Nunavut | Arctic Bay | Nunavut Arctic Bay | 15 | 0.5 | -51 | 21 | 111 | 136 | 73.03 | -85.17
Nunavut | Arviat | Nunavut Arviat | 5 | 0.6 | -48 | 32 | 108 | 141 | 61.12 | -94.05
Nunavut | Baker Lake | Nunavut Baker Lake | 5 | 0.7 | -52 | 33 | 110 | 142 | 64.32 | -96.02
Nunavut | Eureka | Nunavut Eureka | 5 | 0.3 | -55 | 22 | 120 | 144 | 79.98 | -85.95
Nunavut | Igluligaarjuk/Chesterfield Inlet | Nunavut Igluligaarjuk/Chesterfield Inlet | 10 | 0.7 | -51 | 32 | 112 | 144 | 63.33 | -90.7
Nunavut | Iqaluit | Nunavut Iqaluit | 45 | 0.6 | -48 | 27 | 121 | 151 | 63.73 | -68.5
Nunavut | Iqaluktuuttiaq/Cambridge Bay | Nunavut Iqaluktuuttiaq/Cambridge Bay | 15 | 0.4 | -51 | 27 | 105 | 135 | 69.12 | -105.03
Nunavut | Isachsen | Nunavut Isachsen | 10 | 0.4 | -55 | 21 | 125 | 154 | 78.78 | -103.53
Nunavut | Kangiqiniq/Rankin Inlet | Nunavut Kangiqiniq/Rankin Inlet | 10 | 0.6 | -50 | 31 | 116 | 150 | 62.82 | -92.08
Nunavut | Kanngiqtugaapik/Clyde River | Nunavut Kanngiqtugaapik/Clyde River | 5 | 0.9 | -50 | 25 | 110 | 133 | 70.45 | -68.57
Nunavut | Kugluktuk/Coppermine | Nunavut Kugluktuk/Coppermine | 10 | 0.7 | -50 | 35 | 102 | 133 | 67.83 | -115.08
Nunavut | Nottingham Island | Nunavut Nottingham Island | 30 | 1 | -42 | 24 | 133 | 168 | 63.1 | -78
Nunavut | Resolute | Nunavut Resolute | 25 | 0.4 | -52 | 20 | 115 | 142 | 74.68 | -94.9
Nunavut | Resolution Island | Nunavut Resolution Island | 5 | 1.1 | -42 | 23 | 166 | 207 | 61.3 | -64.88
Nunavut | Salliq/Coral Harbour | Nunavut Salliq/Coral Harbour | 15 | 0.8 | -54 | 28 | 114 | 145 | 64.13 | -83.17

## CSA C22.3 No.60826 Table CA.1
Province or Territory | Place Name | For Lookup no overide | Elevation (m) | Latitude | Longitude | Minimum Temperature (oC) | Reference Wind Speed (km/h) | Reference Ice Thickness (mm)
British Columbia | 100 Mile House | British Columbia 100 Mile House | 1040 | 51.65 | -121.28 | –32 | 89 | 10
British Columbia | Abbotsford | British Columbia Abbotsford | 70 | 49.05 | -122.33 | –10 | 99 | 23
British Columbia | Agassiz | British Columbia Agassiz | 15 | 49.23 | -121.77 | –11 | 99 | 21
British Columbia | Alberni | British Columbia Alberni | 12 | 49.27 | -124.8 | –8 | 80 | 10
British Columbia | Ashcroft | British Columbia Ashcroft | 305 | 50.72 | -121.28 | –27 | 92 | 10
British Columbia | Bamfield | British Columbia Bamfield | 20 | 48.83 | -125.13 | –4 | 106 | 10
British Columbia | Beatton River | British Columbia Beatton River | 840 | 57.38 | -121.4 | –39 | 80 | 10
British Columbia | Bella Bella | British Columbia Bella Bella | 25 | 52.16 | -128.14 | –7 | 106 | 10
British Columbia | Bella Coola | British Columbia Bella Coola | 40 | 52.37 | -126.75 | –18 | 89 | 10
British Columbia | Burns Lake | British Columbia Burns Lake | 755 | 54.23 | -125.75 | –34 | 80 | 10
British Columbia | Cache Creek | British Columbia Cache Creek | 455 | 50.8 | -121.32 | –27 | 93 | 10
British Columbia | Campbell River | British Columbia Campbell River | 20 | 50.02 | -125.24 | –7 | 108 | 10
British Columbia | Carmi | British Columbia Carmi | 845 | 49.5 | -119.12 | –26 | 92 | 10
British Columbia | Castlegar | British Columbia Castlegar | 430 | 49.32 | -117.67 | –20 | 80 | 10
British Columbia | Chetwynd | British Columbia Chetwynd | 605 | 55.7 | -121.63 | –38 | 89 | 10
British Columbia | Chilliwack | British Columbia Chilliwack | 10 | 49.17 | -121.95 | –11 | 99 | 21
British Columbia | Comox | British Columbia Comox | 15 | 49.68 | -124.93 | –9 | 104 | 10
British Columbia | Courtenay | British Columbia Courtenay | 10 | 49.68 | -124.98 | –9 | 99 | 10
British Columbia | Cranbrook | British Columbia Cranbrook | 910 | 49.5 | -115.77 | –28 | 80 | 10
British Columbia | Crescent Valley | British Columbia Crescent Valley | 585 | 49.45 | -117.55 | –20 | 80 | 10
British Columbia | Crofton | British Columbia Crofton | 5 | 48.87 | -123.65 | –6 | 87 | 10
British Columbia | Dawson Creek | British Columbia Dawson Creek | 665 | 55.77 | -120.23 | –40 | 89 | 10
British Columbia | Dease Lake | British Columbia Dease Lake | 800 | 58.44 | -130 | –40 | 80 | 10
British Columbia | Dog Creek | British Columbia Dog Creek | 450 | 51.58 | -122.3 | –30 | 89 | 10
British Columbia | Duncan | British Columbia Duncan | 10 | 48.78 | -123.7 | –8 | 80 | 10
British Columbia | Elko | British Columbia Elko | 1065 | 49.3 | -115.12 | –31 | 90 | 10
British Columbia | Fernie | British Columbia Fernie | 1010 | 49.5 | -115.07 | –30 | 90 | 10
British Columbia | Fort Nelson | British Columbia Fort Nelson | 465 | 58.83 | -122.7 | –42 | 80 | 10
British Columbia | Fort St. John | British Columbia Fort St. John | 685 | 56.25 | -120.85 | –37 | 89 | 10
British Columbia | Glacier | British Columbia Glacier | 1145 | 51.27 | -117.52 | –30 | 80 | 10
British Columbia | Gold River | British Columbia Gold River | 120 | 49.78 | -126.05 | –11 | 80 | 10
British Columbia | Golden | British Columbia Golden | 790 | 51.3 | -116.97 | –30 | 80 | 10
British Columbia | Grand Forks | British Columbia Grand Forks | 565 | 49.03 | -118.45 | –22 | 80 | 10
British Columbia | Greenwood | British Columbia Greenwood | 745 | 49.1 | -118.68 | –23 | 87 | 10
British Columbia | Hope | British Columbia Hope | 40 | 49.38 | -121.44 | –15 | 110 | 20
British Columbia | Jordan River | British Columbia Jordan River | 20 | 48.42 | -124.05 | –3 | 111 | 10
British Columbia | Kamloops | British Columbia Kamloops | 355 | 50.67 | -120.32 | –25 | 95 | 10
British Columbia | Kaslo | British Columbia Kaslo | 545 | 49.92 | -116.92 | –20 | 80 | 10
British Columbia | Kelowna | British Columbia Kelowna | 350 | 49.88 | -119.48 | –20 | 95 | 10
British Columbia | Kimberley | British Columbia Kimberley | 1090 | 49.68 | -115.98 | –27 | 80 | 10
British Columbia | Kitimat Plant | British Columbia Kitimat Plant | 15 | 54.05 | -128.63 | –18 | 99 | 20
British Columbia | Kitimat Townsite | British Columbia Kitimat Townsite | 130 | 54.07 | -128.65 | –18 | 99 | 20
British Columbia | Ladysmith | British Columbia Ladysmith | 80 | 48.99 | -123.82 | –9 | 89 | 10
British Columbia | Langford | British Columbia Langford | 80 | 48.45 | -123.5 | –6 | 95 | 10
British Columbia | Lillooet | British Columbia Lillooet | 245 | 50.68 | -121.93 | –23 | 89 | 10
British Columbia | Lytton | British Columbia Lytton | 325 | 50.23 | -121.57 | –20 | 99 | 10
British Columbia | Mackenzie | British Columbia Mackenzie | 765 | 55.3 | -123.08 | –38 | 85 | 10
British Columbia | Masset | British Columbia Masset | 10 | 54.02 | -132.1 | –7 | 118 | 10
British Columbia | McBride | British Columbia McBride | 730 | 53.3 | -120.17 | –32 | 80 | 10
British Columbia | McLeod Lake | British Columbia McLeod Lake | 695 | 54.98 | -123.03 | –37 | 85 | 10
British Columbia | Merritt | British Columbia Merritt | 570 | 50.1 | -120.78 | –27 | 99 | 10
British Columbia | Mission City | British Columbia Mission City | 45 | 49.13 | -122.3 | –11 | 99 | 20
British Columbia | Montrose | British Columbia Montrose | 615 | 49.08 | -117.58 | –18 | 80 | 10
British Columbia | Nakusp | British Columbia Nakusp | 445 | 50.23 | -117.8 | –22 | 80 | 10
British Columbia | Nanaimo | British Columbia Nanaimo | 15 | 49.17 | -123.93 | –8 | 90 | 10
British Columbia | Nelson | British Columbia Nelson | 600 | 49.48 | -117.28 | –20 | 80 | 10
British Columbia | Ocean Falls | British Columbia Ocean Falls | 10 | 52.35 | -127.7 | –12 | 99 | 10
British Columbia | Osoyoos | British Columbia Osoyoos | 285 | 49.03 | -119.5 | –17 | 95 | 10
British Columbia | Parksville | British Columbia Parksville | 40 | 49.32 | -124.33 | –6 | 190 | 10
British Columbia | Penticton | British Columbia Penticton | 350 | 49.5 | -119.58 | –17 | 99 | 10
British Columbia | Port Alberni | British Columbia Port Alberni | 15 | 49.23 | -124.8 | –8 | 80 | 10
British Columbia | Port Alice | British Columbia Port Alice | 25 | 50.38 | -127.45 | –6 | 80 | 10
British Columbia | Port Hardy | British Columbia Port Hardy | 5 | 50.7 | -127.42 | –7 | 108 | 10
British Columbia | Port McNeill | British Columbia Port McNeill | 5 | 50.58 | -127.1 | –7 | 108 | 10
British Columbia | Port Renfrew | British Columbia Port Renfrew | 20 | 48.56 | -124.4 | –5 | 108 | 10
British Columbia | Powell River | British Columbia Powell River | 10 | 49.83 | -124.52 | –9 | 107 | 10
British Columbia | Prince George | British Columbia Prince George | 580 | 53.92 | -122.75 | –36 | 89 | 10
British Columbia | Prince Rupert | British Columbia Prince Rupert | 20 | 54.32 | -130.32 | –15 | 110 | 10
British Columbia | Princeton | British Columbia Princeton | 655 | 49.5 | -120.51 | –29 | 90 | 10
British Columbia | Qualicum Beach | British Columbia Qualicum Beach | 10 | 49.35 | -124.45 | –9 | 90 | 10
British Columbia | Queen Charlotte City | British Columbia Queen Charlotte City | 35 | 53.26 | -132.08 | –8 | 118 | 10
British Columbia | Quesnel | British Columbia Quesnel | 475 | 52.98 | -122.48 | –33 | 84 | 10
British Columbia | Revelstoke | British Columbia Revelstoke | 440 | 50.98 | -118.2 | –23 | 85 | 10
British Columbia | Salmon Arm | British Columbia Salmon Arm | 425 | 50.7 | -119.28 | –24 | 93 | 10
British Columbia | Sandspit | British Columbia Sandspit | 5 | 53.25 | -131.82 | –6 | 133 | 10
British Columbia | Sechelt | British Columbia Sechelt | 25 | 49.47 | -123.75 | –8 | 104 | 10
British Columbia | Sidney | British Columbia Sidney | 10 | 48.65 | -123.4 | –6 | 89 | 10
British Columbia | Smith River | British Columbia Smith River | 660 | 59.88 | -126.43 | –47 | 80 | 10
British Columbia | Smithers | British Columbia Smithers | 500 | 54.78 | -127.17 | –31 | 85 | 10
British Columbia | Sooke | British Columbia Sooke | 20 | 48.38 | -123.72 | –3 | 104 | 10
British Columbia | Squamish | British Columbia Squamish | 5 | 49.7 | -123.15 | –11 | 106 | 10
British Columbia | Stewart | British Columbia Stewart | 10 | 55.93 | -129.98 | –20 | 80 | 10
British Columbia | Tahsis | British Columbia Tahsis | 25 | 49.93 | -126.65 | –6 | 80 | 10
British Columbia | Taylor | British Columbia Taylor | 515 | 56.2 | -120.69 | –37 | 89 | 10
British Columbia | Terrace | British Columbia Terrace | 60 | 54.52 | -128.6 | –21 | 90 | 24
British Columbia | Tofino | British Columbia Tofino | 10 | 49.12 | -125.88 | –4 | 117 | 10
British Columbia | Trail | British Columbia Trail | 440 | 49.1 | -117.7 | –18 | 80 | 10
British Columbia | Ucluelet | British Columbia Ucluelet | 5 | 48.93 | -125.55 | –4 | 124 | 10
Greater Vancouver | Burnaby (Simon Fraser Univ.) | Greater Vancouver Burnaby (Simon Fraser Univ.) | 330 | 49.28 | -122.92 | –9 | 99 | 10
Greater Vancouver | Cloverdale | Greater Vancouver Cloverdale | 10 | 49.1 | -122.73 | –10 | 99 | 10
Greater Vancouver | Haney | Greater Vancouver Haney | 10 | 49.22 | -122.6 | –11 | 99 | 10
Greater Vancouver | Ladner | Greater Vancouver Ladner | 3 | 49.08 | -123.08 | –8 | 99 | 10
Greater Vancouver | Langley | Greater Vancouver Langley | 15 | 49.1 | -122.65 | –10 | 99 | 10
Greater Vancouver | New Westminster | Greater Vancouver New Westminster | 10 | 49.22 | -122.92 | –10 | 99 | 10
Greater Vancouver | North Vancouver | Greater Vancouver North Vancouver | 135 | 49.32 | -123.07 | –9 | 99 | 10
Greater Vancouver | Richmond | Greater Vancouver Richmond | 5 | 49.17 | -123.1 | –9 | 99 | 10
Greater Vancouver | Surrey (88 Ave. & 156 St.) | Greater Vancouver Surrey (88 Ave. & 156 St.) | 90 | 49.16 | -122.79 | –10 | 99 | 10
Greater Vancouver | Vancouver (city hall) | Greater Vancouver Vancouver (city hall) | 40 | 49.25 | -123.12 | –9 | 99 | 10
Greater Vancouver | Vancouver (Granville & 41 Ave.) | Greater Vancouver Vancouver (Granville & 41 Ave.) | 120 | 49.23 | -123.14 | –8 | 99 | 10
Greater Vancouver | West Vancouver | Greater Vancouver West Vancouver | 45 | 49.33 | -123.17 | –9 | 99 | 10
Greater Vancouver | Vernon | Greater Vancouver Vernon | 405 | 50.3 | -119.27 | –23 | 95 | 10
Greater Vancouver | Victoria | Greater Vancouver Victoria | 10 | 48.43 | -123.37 | –6 | 110 | 10
Greater Vancouver | Victoria Gonzales Height | Greater Vancouver Victoria Gonzales Height | 65 | 48.42 | -123.32 | –6 | 110 | 10
Greater Vancouver | Victoria Mt Tolmie | Greater Vancouver Victoria Mt Tolmie | 125 | 48.47 | -123.33 | –8 | 119 | 10
Greater Vancouver | Whistler | Greater Vancouver Whistler | 665 | 50.12 | -122.96 | –23 | 85 | 10
Greater Vancouver | White Rock | Greater Vancouver White Rock | 30 | 49.02 | -122.8 | –7 | 99 | 10
Greater Vancouver | Williams Lake | Greater Vancouver Williams Lake | 615 | 52.13 | -122.15 | –33 | 89 | 10
Greater Vancouver | Youbou | Greater Vancouver Youbou | 200 | 48.88 | -124.2 | –8 | 80 | 10
Alberta | Athabasca | Alberta Athabasca | 515 | 54.72 | -113.28 | –38 | 89 | 10
Alberta | Banff | Alberta Banff | 1400 | 51.17 | -115.57 | –33 | 85 | 10
Alberta | Barrhead | Alberta Barrhead | 645 | 54.13 | -114.4 | –36 | 89 | 10
Alberta | Beaverlodge | Alberta Beaverlodge | 730 | 55.22 | -119.43 | –39 | 90 | 10
Alberta | Brooks | Alberta Brooks | 760 | 50.58 | -111.88 | –34 | 99 | 10
Alberta | Calgary | Alberta Calgary | 1045 | 51.05 | -114.08 | –32 | 99 | 10
Alberta | Campsie | Alberta Campsie | 660 | 54.13 | -114.65 | –36 | 89 | 10
Alberta | Camrose | Alberta Camrose | 740 | 53.02 | -112.83 | –35 | 93 | 10
Alberta | Canmore | Alberta Canmore | 1320 | 51.09 | -115.35 | –33 | 91 | 10
Alberta | Cardston | Alberta Cardston | 1130 | 49.2 | -113.3 | –32 | 127 | 10
Alberta | Claresholm | Alberta Claresholm | 1030 | 50.03 | -113.58 | –32 | 115 | 10
Alberta | Cold Lake | Alberta Cold Lake | 540 | 54.45 | -110.17 | –38 | 89 | 10
Alberta | Coleman | Alberta Coleman | 1320 | 49.63 | -114.5 | –34 | 99 | 10
Alberta | Coronation | Alberta Coronation | 790 | 52.08 | -111.45 | –34 | 91 | 10
Alberta | Cowley | Alberta Cowley | 1175 | 49.57 | -114.08 | –32 | 140 | 10
Alberta | Drumheller | Alberta Drumheller | 685 | 51.47 | -112.7 | –34 | 99 | 10
Alberta | Edmonton | Alberta Edmonton | 645 | 53.55 | -113.47 | –33 | 89 | 10
Alberta | Edson | Alberta Edson | 920 | 53.58 | -116.43 | –37 | 90 | 10
Alberta | Embarras Portage | Alberta Embarras Portage | 220 | 58.45 | -111.47 | –43 | 80 | 10
Alberta | Fairview | Alberta Fairview | 670 | 56.07 | -118.38 | –40 | 89 | 10
Alberta | Fort MacLeod | Alberta Fort MacLeod | 945 | 49.72 | -113.42 | –32 | 125 | 10
Alberta | Fort McMurray | Alberta Fort McMurray | 255 | 56.73 | -111.38 | –40 | 80 | 10
Alberta | Fort Saskatchewan | Alberta Fort Saskatchewan | 610 | 53.72 | -113.22 | –35 | 89 | 10
Alberta | Fort Vermilion | Alberta Fort Vermilion | 270 | 58.4 | -116 | –43 | 80 | 10
Alberta | Grande Prairie | Alberta Grande Prairie | 650 | 55.17 | -118.8 | –39 | 99 | 10
Alberta | Habay | Alberta Habay | 335 | 58.83 | -118.73 | –43 | 80 | 10
Alberta | Hardisty | Alberta Hardisty | 615 | 52.67 | -111.3 | –36 | 90 | 10
Alberta | High River | Alberta High River | 1040 | 50.58 | -113.87 | –32 | 109 | 10
Alberta | Hinton | Alberta Hinton | 990 | 53.4 | -117.58 | –38 | 90 | 10
Alberta | Jasper | Alberta Jasper | 1060 | 52.88 | -118.08 | –34 | 80 | 10
Alberta | Keg River | Alberta Keg River | 420 | 57.75 | -117.62 | –42 | 80 | 10
Alberta | Lac la Biche | Alberta Lac la Biche | 560 | 54.77 | -111.97 | –38 | 89 | 10
Alberta | Lacombe | Alberta Lacombe | 855 | 52.47 | -113.73 | –36 | 95 | 10
Alberta | Lethbridge | Alberta Lethbridge | 910 | 49.7 | -112.82 | –32 | 109 | 10
Alberta | Manning | Alberta Manning | 465 | 56.92 | -117.62 | –41 | 80 | 10
Alberta | Medicine Hat | Alberta Medicine Hat | 705 | 50.05 | -110.67 | –34 | 99 | 10
Alberta | Peace River | Alberta Peace River | 330 | 56.23 | -117.28 | –40 | 85 | 10
Alberta | Pincher Creek | Alberta Pincher Creek | 1130 | 49.48 | -113.95 | –32 | 140 | 10
Alberta | Ranfurly | Alberta Ranfurly | 670 | 53.42 | -111.68 | –37 | 89 | 10
Alberta | Red Deer | Alberta Red Deer | 855 | 52.27 | -113.8 | –35 | 95 | 10
Alberta | Rocky Mountain House | Alberta Rocky Mountain House | 985 | 52.37 | -114.92 | –34 | 90 | 10
Alberta | Slave Lake | Alberta Slave Lake | 590 | 55.28 | -114.77 | –38 | 89 | 10
Alberta | Stettler | Alberta Stettler | 820 | 52.32 | -112.72 | –34 | 90 | 10
Alberta | Stony Plain | Alberta Stony Plain | 710 | 53.53 | -114 | –35 | 89 | 10
Alberta | Suffield | Alberta Suffield | 755 | 50.2 | -111.17 | –34 | 99 | 10
Alberta | Taber | Alberta Taber | 815 | 49.78 | -112.15 | –33 | 109 | 10
Alberta | Turner Valley | Alberta Turner Valley | 1215 | 50.67 | -114.28 | –32 | 100 | 10
Alberta | Valleyview | Alberta Valleyview | 700 | 55.07 | -117.28 | –40 | 98 | 10
Alberta | Vegreville | Alberta Vegreville | 635 | 53.5 | -112.05 | –37 | 89 | 10
Alberta | Vermilion | Alberta Vermilion | 580 | 53.37 | -110.85 | –38 | 90 | 10
Alberta | Wagner | Alberta Wagner | 585 | 55.35 | -114.98 | –38 | 89 | 10
Alberta | Wainwright | Alberta Wainwright | 675 | 52.82 | -110.87 | –36 | 90 | 10
Alberta | Wetaskiwin | Alberta Wetaskiwin | 760 | 52.97 | -113.37 | –35 | 93 | 10
Alberta | Whitecourt | Alberta Whitecourt | 690 | 54.15 | -115.68 | –36 | 91 | 10
Alberta | Wimborne | Alberta Wimborne | 975 | 51.87 | -113.58 | –34 | 95 | 10
Saskatchewan | Assiniboia | Saskatchewan Assiniboia | 740 | 49.63 | -105.98 | –34 | 100 | 10
Saskatchewan | Battrum | Saskatchewan Battrum | 700 | 50.55 | -108.33 | –34 | 110 | 10
Saskatchewan | Biggar | Saskatchewan Biggar | 645 | 52.07 | -108 | –36 | 99 | 10
Saskatchewan | Broadview | Saskatchewan Broadview | 600 | 50.37 | -102.58 | –35 | 99 | 10
Saskatchewan | Dafoe | Saskatchewan Dafoe | 530 | 51.75 | -104.53 | –37 | 91 | 10
Saskatchewan | Dundurn | Saskatchewan Dundurn | 525 | 51.82 | -106.5 | –37 | 102 | 10
Saskatchewan | Estevan | Saskatchewan Estevan | 565 | 49.13 | -102.98 | –34 | 108 | 10
Saskatchewan | Hudson Bay | Saskatchewan Hudson Bay | 370 | 52.85 | -102.38 | –38 | 88 | 10
Saskatchewan | Humbolt | Saskatchewan Humbolt | 565 | 52.2 | -105.12 | –38 | 89 | 10
Saskatchewan | Island Falls | Saskatchewan Island Falls | 305 | 55.53 | -102.35 | –41 | 80 | 10
Saskatchewan | Kamsack | Saskatchewan Kamsack | 455 | 51.57 | -101.9 | –37 | 95 | 10
Saskatchewan | Kindersley | Saskatchewan Kindersley | 685 | 51.47 | -109.17 | –35 | 102 | 10
Saskatchewan | Lloydminster | Saskatchewan Lloydminster | 645 | 53.28 | -110 | –37 | 90 | 10
Saskatchewan | Maple Creek | Saskatchewan Maple Creek | 765 | 49.92 | -109.48 | –34 | 99 | 10
Saskatchewan | Meadow Lake | Saskatchewan Meadow Lake | 480 | 54.13 | -108.43 | –40 | 88 | 10
Saskatchewan | Melfort | Saskatchewan Melfort | 455 | 52.87 | -104.62 | –38 | 88 | 10
Saskatchewan | Melville | Saskatchewan Melville | 550 | 50.92 | -102.8 | –36 | 95 | 10
Saskatchewan | Moose Jaw | Saskatchewan Moose Jaw | 545 | 50.4 | -105.53 | –34 | 108 | 10
Saskatchewan | Nipawin | Saskatchewan Nipawin | 365 | 53.37 | -104 | –39 | 88 | 10
Saskatchewan | North Battleford | Saskatchewan North Battleford | 545 | 52.78 | -108.28 | –36 | 90 | 10
Saskatchewan | Prince Albert | Saskatchewan Prince Albert | 435 | 53.2 | -105.77 | –40 | 88 | 10
Saskatchewan | Qu’Appelle | Saskatchewan Qu’Appelle | 645 | 50.55 | -103.88 | –36 | 98 | 10
Saskatchewan | Regina | Saskatchewan Regina | 575 | 50.45 | -104.62 | –36 | 105 | 10
Saskatchewan | Rosetown | Saskatchewan Rosetown | 595 | 51.55 | -108 | –36 | 105 | 10
Saskatchewan | Saskatoon | Saskatchewan Saskatoon | 500 | 52.12 | -106.63 | –37 | 99 | 10
Saskatchewan | Scott | Saskatchewan Scott | 645 | 52.37 | -108.83 | –36 | 99 | 10
Saskatchewan | Strasbourg | Saskatchewan Strasbourg | 545 | 51.07 | -104.95 | –36 | 98 | 10
Saskatchewan | Swift Current | Saskatchewan Swift Current | 750 | 50.28 | -107.8 | –34 | 110 | 10
Saskatchewan | Uranium City | Saskatchewan Uranium City | 265 | 59.57 | -108.62 | –44 | 80 | 10
Saskatchewan | Weyburn | Saskatchewan Weyburn | 575 | 49.67 | -103.85 | –35 | 99 | 10
Saskatchewan | Yorkton | Saskatchewan Yorkton | 510 | 51.22 | -102.47 | –37 | 95 | 10
Manitoba | Beausejour | Manitoba Beausejour | 245 | 50.07 | -96.52 | –35 | 96 | 16
Manitoba | Boissevain | Manitoba Boissevain | 510 | 49.23 | -100.05 | –34 | 108 | 14
Manitoba | Brandon | Manitoba Brandon | 395 | 49.83 | -99.95 | –35 | 99 | 14
Manitoba | Churchill | Manitoba Churchill | 10 | 58.75 | -94.12 | –40 | 109 | 21
Manitoba | Dauphin | Manitoba Dauphin | 295 | 51.15 | -100.05 | –35 | 90 | 13
Manitoba | Flin Flon | Manitoba Flin Flon | 300 | 54.77 | -101.88 | –40 | 80 | 12
Manitoba | Gimli | Manitoba Gimli | 220 | 50.64 | -96.99 | –36 | 90 | 16
Manitoba | Island Lake | Manitoba Island Lake | 240 | 53.87 | -94.67 | –38 | 89 | 15
Manitoba | Lac du Bonnet | Manitoba Lac du Bonnet | 260 | 50.27 | -96.06 | –36 | 80 | 16
Manitoba | Lynn Lake | Manitoba Lynn Lake | 350 | 56.85 | -101.05 | –42 | 80 | 12
Manitoba | Morden | Manitoba Morden | 300 | 49.18 | -98.1 | –33 | 108 | 16
Manitoba | Neepawa | Manitoba Neepawa | 365 | 50.23 | -99.47 | –34 | 99 | 15
Manitoba | Pine Falls | Manitoba Pine Falls | 220 | 50.57 | -96.22 | –36 | 80 | 16
Manitoba | Portage la Prairie | Manitoba Portage la Prairie | 260 | 50 | -98.29 | –33 | 99 | 14
Manitoba | Rivers | Manitoba Rivers | 465 | 50.03 | -100.23 | –36 | 99 | 13
Manitoba | Sandilands | Manitoba Sandilands | 365 | 49.36 | -96.3 | –34 | 89 | 16
Manitoba | Selkirk | Manitoba Selkirk | 225 | 50.15 | -96.87 | –35 | 96 | 16
Manitoba | Split Lake | Manitoba Split Lake | 175 | 56.25 | -96.1 | –40 | 89 | 18
Manitoba | Steinbach | Manitoba Steinbach | 270 | 49.53 | -96.68 | –35 | 95 | 16
Manitoba | Swan River | Manitoba Swan River | 335 | 52.14 | -101.27 | –37 | 89 | 14
Manitoba | The Pas | Manitoba The Pas | 270 | 53.87 | -101.25 | –38 | 89 | 12
Manitoba | Thompson | Manitoba Thompson | 205 | 55.79 | -97.86 | –43 | 87 | 12
Manitoba | Virden | Manitoba Virden | 435 | 49.86 | -100.93 | –35 | 99 | 14
Manitoba | Winnipeg | Manitoba Winnipeg | 235 | 49.89 | -97.15 | –35 | 99 | 16
Ontario | Ailsa Craig | Ontario Ailsa Craig | 230 | 43.13 | -81.55 | –19 | 106 | 24
Ontario | Ajax | Ontario Ajax | 95 | 43.85 | -79.03 | –22 | 99 | 20
Ontario | Alexandria | Ontario Alexandria | 80 | 45.32 | -74.63 | –26 | 95 | 30
Ontario | Alliston | Ontario Alliston | 220 | 44.15 | -79.87 | –25 | 92 | 23
Ontario | Almonte | Ontario Almonte | 120 | 45.23 | -76.2 | –28 | 87 | 26
Ontario | Armstrong | Ontario Armstrong | 340 | 50.3 | -89.03 | –40 | 80 | 15
Ontario | Arnprior | Ontario Arnprior | 85 | 45.43 | -76.35 | –29 | 89 | 27
Ontario | Atikokan | Ontario Atikokan | 400 | 48.75 | -91.62 | –35 | 80 | 15
Ontario | Attawapiskat | Ontario Attawapiskat | 10 | 52.93 | -82.43 | –39 | 96 | 17
Ontario | Aurora | Ontario Aurora | 270 | 44 | -79.47 | –23 | 99 | 23
Ontario | Bancroft | Ontario Bancroft | 365 | 45.05 | -77.85 | –31 | 85 | 23
Ontario | Barrie | Ontario Barrie | 245 | 44.4 | -79.67 | –26 | 90 | 23
Ontario | Barriefield | Ontario Barriefield | 100 | 44.23 | -76.47 | –24 | 103 | 30
Ontario | Beaverton | Ontario Beaverton | 240 | 44.43 | -79.15 | –26 | 90 | 23
Ontario | Belleville | Ontario Belleville | 90 | 44.17 | -77.38 | –24 | 99 | 22
Ontario | Belmont | Ontario Belmont | 260 | 42.88 | -81.08 | –19 | 99 | 30
Ontario | Bowmanville | Ontario Bowmanville | 95 | 43.91 | -78.68 | –22 | 104 | 20
Ontario | Bracebridge | Ontario Bracebridge | 310 | 45.03 | -79.3 | –28 | 89 | 21
Ontario | Bradford | Ontario Bradford | 240 | 44.12 | -79.57 | –25 | 92 | 24
Ontario | Brampton | Ontario Brampton | 215 | 43.68 | -79.77 | –21 | 99 | 25
Ontario | Brantford | Ontario Brantford | 205 | 43.13 | -80.27 | –20 | 98 | 25
Ontario | Brighton | Ontario Brighton | 95 | 44.03 | -77.73 | –23 | 104 | 22
Ontario | Brockville | Ontario Brockville | 85 | 44.59 | -75.68 | –25 | 100 | 30
Ontario | Burk’s Falls | Ontario Burk’s Falls | 305 | 45.62 | -79.4 | –28 | 80 | 22
Ontario | Burlington | Ontario Burlington | 80 | 43.32 | -79.8 | –19 | 99 | 22
Ontario | Cambridge | Ontario Cambridge | 295 | 43.38 | -80.32 | –20 | 90 | 25
Ontario | Campbellford | Ontario Campbellford | 150 | 44.3 | -77.8 | –26 | 96 | 22
Ontario | Cannington | Ontario Cannington | 255 | 44.35 | -79.03 | –26 | 90 | 25
Ontario | Carleton Place | Ontario Carleton Place | 135 | 45.13 | -76.15 | –27 | 87 | 27
Ontario | Cavan | Ontario Cavan | 200 | 44.2 | -78.47 | –25 | 96 | 25
Ontario | Centralia | Ontario Centralia | 260 | 43.28 | -81.47 | –19 | 100 | 21
Ontario | CFB Borden | Ontario CFB Borden | 225 | 44.27 | -79.88 | –25 | 92 | 22
Ontario | Chapleau | Ontario Chapleau | 425 | 47.83 | -83.4 | –38 | 80 | 21
Ontario | Chatham | Ontario Chatham | 180 | 42.4 | -82.18 | –18 | 99 | 28
Ontario | Chesley | Ontario Chesley | 275 | 44.28 | -81.08 | –21 | 99 | 21
Ontario | Clinton | Ontario Clinton | 280 | 43.62 | -81.53 | –19 | 105 | 21
Ontario | Coboconk | Ontario Coboconk | 270 | 44.65 | -78.8 | –27 | 89 | 23
Ontario | Cobourg | Ontario Cobourg | 90 | 43.97 | -78.17 | –23 | 105 | 20
Ontario | Cochrane | Ontario Cochrane | 245 | 49.07 | -81.02 | –36 | 80 | 17
Ontario | Colborne | Ontario Colborne | 105 | 44 | -77.88 | –23 | 105 | 20
Ontario | Collingwood | Ontario Collingwood | 190 | 44.48 | -80.22 | –23 | 93 | 20
Ontario | Cornwall | Ontario Cornwall | 35 | 45.03 | -74.73 | –25 | 96 | 30
Ontario | Corunna | Ontario Corunna | 185 | 42.88 | -82.43 | –18 | 103 | 22
Ontario | Deep River | Ontario Deep River | 145 | 46.1 | -77.5 | –32 | 89 | 22
Ontario | Deseronto | Ontario Deseronto | 85 | 44.2 | -77.05 | –24 | 99 | 25
Ontario | Dorchester | Ontario Dorchester | 260 | 42.98 | -81.07 | –20 | 99 | 30
Ontario | Dorion | Ontario Dorion | 200 | 48.78 | -88.53 | –35 | 93 | 16
Ontario | Dresden | Ontario Dresden | 185 | 42.58 | -82.18 | –18 | 99 | 25
Ontario | Dryden | Ontario Dryden | 370 | 49.78 | -92.75 | –36 | 80 | 15
Ontario | Dundalk | Ontario Dundalk | 525 | 44.17 | -80.39 | –24 | 98 | 24
Ontario | Dunnville | Ontario Dunnville | 175 | 42.9 | -79.62 | –17 | 102 | 25
Ontario | Durham | Ontario Durham | 340 | 44.17 | -80.82 | –22 | 99 | 24
Ontario | Dutton | Ontario Dutton | 225 | 42.67 | -81.5 | –18 | 99 | 26
Ontario | Earlton | Ontario Earlton | 245 | 47.72 | -79.82 | –36 | 89 | 21
Ontario | Edison | Ontario Edison | 365 | 49.8 | -93.55 | –36 | 80 | 15
Ontario | Elliot Lake | Ontario Elliot Lake | 380 | 46.38 | -82.66 | –28 | 92 | 24
Ontario | Elmvale | Ontario Elmvale | 220 | 44.58 | -79.87 | –26 | 90 | 21
Ontario | Embro | Ontario Embro | 310 | 43.15 | -80.9 | –21 | 99 | 28
Ontario | Englehart | Ontario Englehart | 205 | 47.82 | -79.87 | –36 | 89 | 21
Ontario | Espanola | Ontario Espanola | 220 | 46.25 | -81.77 | –27 | 98 | 24
Ontario | Exeter | Ontario Exeter | 265 | 43.35 | -81.48 | –19 | 100 | 22
Ontario | Fenelon Falls | Ontario Fenelon Falls | 260 | 44.53 | -78.75 | –27 | 90 | 25
Ontario | Fergus | Ontario Fergus | 400 | 43.7 | -80.37 | –22 | 92 | 25
Ontario | Forest | Ontario Forest | 215 | 43.1 | -82 | –18 | 104 | 22
Ontario | Fort Erie | Ontario Fort Erie | 180 | 42.9 | -78.93 | –17 | 102 | 27
Ontario | Fort Erie (Ridgeway) | Ontario Fort Erie (Ridgeway) | 190 | 42.88 | -79.05 | –17 | 102 | 27
Ontario | Fort Frances | Ontario Fort Frances | 340 | 48.61 | -93.39 | –35 | 80 | 15
Ontario | Gananoque | Ontario Gananoque | 80 | 44.33 | -76.17 | –24 | 103 | 30
Ontario | Geraldton | Ontario Geraldton | 345 | 49.73 | -86.95 | –39 | 80 | 15
Ontario | Glencoe | Ontario Glencoe | 215 | 42.75 | -81.72 | –18 | 99 | 26
Ontario | Goderich | Ontario Goderich | 185 | 43.75 | -81.72 | –18 | 111 | 20
Ontario | Gore Bay | Ontario Gore Bay | 205 | 45.92 | -82.47 | –26 | 100 | 21
Ontario | Graham | Ontario Graham | 495 | 49.25 | -90.57 | –37 | 80 | 15
Ontario | Gravenhurst (Muskoka Airport) | Ontario Gravenhurst (Muskoka Airport) | 255 | 44.92 | -79.37 | –28 | 88 | 21
Ontario | Grimsby | Ontario Grimsby | 85 | 43.2 | -79.57 | –18 | 102 | 25
Ontario | Guelph | Ontario Guelph | 340 | 43.55 | -80.25 | –21 | 92 | 25
Ontario | Guthrie | Ontario Guthrie | 280 | 44.47 | -79.55 | –26 | 90 | 23
Ontario | Haileybury | Ontario Haileybury | 210 | 47.45 | -79.63 | –35 | 89 | 22
Ontario | Haldimand (Caledonia) | Ontario Haldimand (Caledonia) | 190 | 43.07 | -79.93 | –20 | 100 | 28
Ontario | Haldimand (Hagersville) | Ontario Haldimand (Hagersville) | 215 | 42.97 | -80.05 | –19 | 102 | 30
Ontario | Haliburton | Ontario Haliburton | 335 | 45.05 | -78.52 | –29 | 89 | 23
Ontario | Halton Hills (Georgetown) | Ontario Halton Hills (Georgetown) | 255 | 43.65 | -79.92 | –21 | 92 | 25
Ontario | Hamilton | Ontario Hamilton | 90 | 43.25 | -79.86 | –19 | 99 | 25
Ontario | Hanover | Ontario Hanover | 270 | 44.15 | -81.03 | –21 | 99 | 22
Ontario | Hastings | Ontario Hastings | 200 | 44.3 | -77.95 | –26 | 96 | 25
Ontario | Hawkesbury | Ontario Hawkesbury | 50 | 45.6 | -74.62 | –27 | 96 | 30
Ontario | Hearst | Ontario Hearst | 245 | 49.68 | -83.67 | –37 | 80 | 15
Ontario | Honey Harbour | Ontario Honey Harbour | 180 | 44.87 | -79.82 | –26 | 93 | 20
Ontario | Hornepayne | Ontario Hornepayne | 360 | 49.22 | -84.78 | –40 | 80 | 15
Ontario | Huntsville | Ontario Huntsville | 335 | 45.33 | -79.22 | –29 | 80 | 22
Ontario | Ingersoll | Ontario Ingersoll | 280 | 43.03 | -80.88 | –20 | 99 | 30
Ontario | Iroquois Falls | Ontario Iroquois Falls | 275 | 48.77 | -80.68 | –36 | 87 | 18
Ontario | Jellicoe | Ontario Jellicoe | 330 | 49.68 | -87.52 | –39 | 80 | 15
Ontario | Kapuskasing | Ontario Kapuskasing | 245 | 49.42 | -82.43 | –36 | 80 | 15
Ontario | Kemptville | Ontario Kemptville | 90 | 45.02 | -75.64 | –27 | 87 | 30
Ontario | Kenora | Ontario Kenora | 370 | 49.82 | -94.43 | –35 | 80 | 15
Ontario | Killaloe | Ontario Killaloe | 185 | 45.55 | -77.42 | –31 | 89 | 20
Ontario | Kincardine | Ontario Kincardine | 190 | 44.18 | -81.63 | –19 | 111 | 20
Ontario | Kingston | Ontario Kingston | 80 | 44.23 | -76.48 | –24 | 103 | 30
Ontario | Kinmount | Ontario Kinmount | 295 | 44.78 | -78.65 | –28 | 89 | 24
Ontario | Kirkland Lake | Ontario Kirkland Lake | 325 | 48.15 | -80.03 | –36 | 89 | 21
Ontario | Kitchener | Ontario Kitchener | 335 | 43.45 | -80.48 | –21 | 91 | 26
Ontario | Kitchenuhmaykoosib | Ontario Kitchenuhmaykoosib | 215 | 53.83 | -90 | –40 | 95 | 18
Ontario | Lakefield | Ontario Lakefield | 240 | 44.43 | -78.27 | –26 | 92 | 25
Ontario | Lansdowne House | Ontario Lansdowne House | 240 | 52.23 | -87.88 | –40 | 85 | 15
Ontario | Leamington | Ontario Leamington | 190 | 42.08 | -82.57 | –17 | 99 | 28
Ontario | Lindsay | Ontario Lindsay | 265 | 44.35 | -78.73 | –26 | 89 | 25
Ontario | Lion’s Head | Ontario Lion’s Head | 185 | 44.98 | -81.25 | –21 | 104 | 18
Ontario | Listowel | Ontario Listowel | 380 | 43.73 | -80.95 | –21 | 99 | 23
Ontario | London | Ontario London | 245 | 42.98 | -81.23 | –20 | 99 | 30
Ontario | Lucan | Ontario Lucan | 300 | 43.18 | -81.4 | –19 | 99 | 25
Ontario | Maitland | Ontario Maitland | 85 | 44.63 | -75.62 | –25 | 100 | 30
Ontario | Markdale | Ontario Markdale | 425 | 44.32 | -80.65 | –22 | 96 | 22
Ontario | Markham | Ontario Markham | 175 | 43.87 | -79.27 | –23 | 99 | 25
Ontario | Martin | Ontario Martin | 485 | 49.25 | -91.13 | –37 | 80 | 15
Ontario | Matheson | Ontario Matheson | 265 | 48.53 | -80.47 | –36 | 89 | 19
Ontario | Mattawa | Ontario Mattawa | 165 | 46.32 | -78.7 | –31 | 85 | 23
Ontario | Midland | Ontario Midland | 190 | 44.75 | -79.88 | –26 | 93 | 20
Ontario | Milton | Ontario Milton | 200 | 43.52 | -79.88 | –20 | 92 | 25
Ontario | Milverton | Ontario Milverton | 370 | 43.57 | -80.92 | –21 | 99 | 25
Ontario | Minden | Ontario Minden | 270 | 44.92 | -78.73 | –29 | 89 | 25
Ontario | Mississauga | Ontario Mississauga | 160 | 43.58 | -79.65 | –20 | 99 | 25
Ontario | Mississauga Port Credit | Ontario Mississauga Port Credit | 75 | 43.55 | -79.58 | –20 | 99 | 22
Ontario | Mitchell | Ontario Mitchell | 335 | 43.47 | -81.2 | –20 | 99 | 24
Ontario | Moosonee | Ontario Moosonee | 10 | 51.32 | -80.72 | –38 | 89 | 15
Ontario | Morrisburg | Ontario Morrisburg | 75 | 44.9 | -75.18 | –25 | 96 | 30
Ontario | Mount Forest | Ontario Mount Forest | 420 | 43.98 | -80.73 | –24 | 96 | 24
Ontario | Nakina | Ontario Nakina | 325 | 50.17 | -86.7 | –38 | 80 | 15
Ontario | Nanticoke (Jarvis) | Ontario Nanticoke (Jarvis) | 205 | 42.88 | -80.1 | –18 | 104 | 30
Ontario | Nanticoke (Port Dover) | Ontario Nanticoke (Port Dover) | 180 | 42.78 | -80.2 | –17 | 104 | 25
Ontario | Napanee | Ontario Napanee | 90 | 44.25 | -76.95 | –24 | 99 | 26
Ontario | New Liskeard | Ontario New Liskeard | 180 | 47.5 | -79.67 | –35 | 89 | 22
Ontario | Newcastle | Ontario Newcastle | 115 | 43.92 | -78.58 | –22 | 104 | 20
Ontario | Newmarket | Ontario Newmarket | 185 | 44.05 | -79.47 | –24 | 92 | 25
Ontario | Niagara Falls | Ontario Niagara Falls | 210 | 43.1 | -79.07 | –18 | 100 | 25
Ontario | North Bay | Ontario North Bay | 210 | 46.32 | -79.47 | –30 | 80 | 23
Ontario | Norwood | Ontario Norwood | 225 | 44.38 | -77.98 | –26 | 96 | 25
Ontario | Oakville | Ontario Oakville | 90 | 43.45 | -79.68 | –20 | 99 | 22
Ontario | Orangeville | Ontario Orangeville | 430 | 43.92 | -80.1 | –23 | 92 | 25
Ontario | Orillia | Ontario Orillia | 230 | 44.62 | -79.42 | –27 | 90 | 22
Ontario | Oshawa | Ontario Oshawa | 110 | 43.9 | -78.85 | –21 | 104 | 20
Ontario | Ottawa (Barrhaven) | Ontario Ottawa (Barrhaven) | 98 | 45.28 | -75.76 | –27 | 89 | 30
Ontario | Ottawa (City Hall) | Ontario Ottawa (City Hall) | 70 | 45.42 | -75.69 | –27 | 90 | 30
Ontario | Ottawa (Kanata) | Ontario Ottawa (Kanata) | 98 | 45.31 | -75.91 | –27 | 89 | 28
Ontario | Ottawa (M–C Int’l Airport) | Ontario Ottawa (M–C Int’l Airport) | 125 | 45.32 | -75.67 | –27 | 90 | 30
Ontario | Ottawa (Orleans) | Ontario Ottawa (Orleans) | 70 | 45.48 | -75.52 | –28 | 96 | 30
Ontario | Owen Sound | Ontario Owen Sound | 215 | 44.57 | -80.93 | –21 | 99 | 21
Ontario | Pagwa River | Ontario Pagwa River | 185 | 50.02 | -85.22 | –37 | 80 | 15
Ontario | Paris | Ontario Paris | 245 | 43.2 | -80.38 | –20 | 98 | 27
Ontario | Parkhill | Ontario Parkhill | 205 | 43.15 | -81.68 | –18 | 100 | 24
Ontario | Parry Sound | Ontario Parry Sound | 215 | 45.35 | -80.03 | –26 | 93 | 18
Ontario | Pelham (Fonthill) | Ontario Pelham (Fonthill) | 230 | 43.03 | -79.28 | –17 | 100 | 25
Ontario | Pembroke | Ontario Pembroke | 125 | 45.82 | -77.12 | –31 | 89 | 24
Ontario | Penetanguishene | Ontario Penetanguishene | 220 | 44.78 | -79.92 | –26 | 93 | 18
Ontario | Perth | Ontario Perth | 130 | 44.9 | -76.25 | –27 | 87 | 26
Ontario | Petawawa | Ontario Petawawa | 135 | 45.9 | -77.33 | –31 | 89 | 24
Ontario | Peterborough | Ontario Peterborough | 200 | 44.3 | -78.32 | –25 | 96 | 25
Ontario | Petrolia | Ontario Petrolia | 195 | 42.87 | -82.15 | –18 | 99 | 22
Ontario | Pickering (Dunbarton) | Ontario Pickering (Dunbarton) | 85 | 43.82 | -79.1 | –21 | 99 | 20
Ontario | Picton | Ontario Picton | 95 | 44 | -77.13 | –23 | 105 | 24
Ontario | Plattsville | Ontario Plattsville | 300 | 43.3 | -80.62 | –21 | 98 | 27
Ontario | Point Alexander | Ontario Point Alexander | 150 | 46.13 | -77.57 | –32 | 89 | 23
Ontario | Port Burwell | Ontario Port Burwell | 195 | 42.65 | -80.82 | –17 | 103 | 26
Ontario | Port Colborne | Ontario Port Colborne | 180 | 42.9 | -79.23 | –17 | 102 | 25
Ontario | Port Elgin | Ontario Port Elgin | 205 | 44.43 | -81.4 | –19 | 111 | 20
Ontario | Port Hope | Ontario Port Hope | 100 | 43.95 | -78.3 | –23 | 104 | 20
Ontario | Port Perry | Ontario Port Perry | 270 | 44.1 | -78.95 | –24 | 99 | 25
Ontario | Port Stanley | Ontario Port Stanley | 180 | 42.67 | -81.22 | –17 | 99 | 25
Ontario | Prescott | Ontario Prescott | 90 | 44.72 | -75.52 | –25 | 100 | 30
Ontario | Princeton | Ontario Princeton | 280 | 43.17 | -80.53 | –20 | 98 | 27
Ontario | Raith | Ontario Raith | 475 | 48.83 | -89.93 | –37 | 80 | 15
Ontario | Rayside–Balfour (Chelmsford) | Ontario Rayside–Balfour (Chelmsford) | 270 | 46.58 | -81.2 | –30 | 90 | 23
Ontario | Red Lake | Ontario Red Lake | 360 | 51.05 | -93.82 | –37 | 80 | 15
Ontario | Renfrew | Ontario Renfrew | 115 | 45.47 | -76.68 | –30 | 89 | 25
Ontario | Richmond Hill | Ontario Richmond Hill | 230 | 43.87 | -79.45 | –23 | 99 | 23
Ontario | Rockland | Ontario Rockland | 50 | 45.55 | -75.29 | –28 | 95 | 30
Ontario | Sarnia | Ontario Sarnia | 190 | 42.97 | -82.38 | –18 | 103 | 22
Ontario | Sault Ste. Marie | Ontario Sault Ste. Marie | 190 | 46.52 | -84.33 | –28 | 100 | 23
Ontario | Schreiber | Ontario Schreiber | 310 | 48.8 | -87.25 | –36 | 93 | 18
Ontario | Seaforth | Ontario Seaforth | 310 | 43.55 | -81.4 | –19 | 100 | 22
Ontario | Shelburne | Ontario Shelburne | 495 | 44.08 | -80.2 | –24 | 94 | 14
Ontario | Simcoe | Ontario Simcoe | 210 | 42.83 | -80.3 | –19 | 101 | 33
Ontario | Sioux Lookout | Ontario Sioux Lookout | 375 | 50.07 | -91.98 | –36 | 80 | 15
Ontario | Smiths Falls | Ontario Smiths Falls | 130 | 44.9 | -76.02 | –27 | 87 | 26
Ontario | Smithville | Ontario Smithville | 185 | 43.1 | -79.55 | –18 | 100 | 25
Ontario | Smooth Rock Falls | Ontario Smooth Rock Falls | 235 | 49.28 | -81.63 | –36 | 80 | 16
Ontario | South River | Ontario South River | 355 | 45.83 | -79.38 | –29 | 80 | 22
Ontario | Southampton | Ontario Southampton | 180 | 44.48 | -81.38 | –19 | 109 | 20
Ontario | St. Catharines | Ontario St. Catharines | 105 | 43.17 | -79.25 | –18 | 102 | 25
Ontario | St. Mary’s | Ontario St. Mary’s | 310 | 43.25 | -81.13 | –20 | 99 | 25
Ontario | St. Thomas | Ontario St. Thomas | 225 | 42.78 | -81.2 | –18 | 99 | 30
Ontario | Stirling | Ontario Stirling | 120 | 44.3 | -77.55 | –25 | 95 | 25
Ontario | Stratford | Ontario Stratford | 360 | 43.37 | -80.95 | –20 | 99 | 27
Ontario | Strathroy | Ontario Strathroy | 225 | 42.95 | -81.63 | –19 | 99 | 27
Ontario | Sturgeon Falls | Ontario Sturgeon Falls | 205 | 46.37 | -79.92 | –30 | 80 | 23
Ontario | Sudbury | Ontario Sudbury | 275 | 46.5 | -81 | –30 | 90 | 22
Ontario | Sundridge | Ontario Sundridge | 340 | 45.77 | -79.4 | –29 | 80 | 22
Ontario | Tavistock | Ontario Tavistock | 340 | 43.32 | -80.83 | –21 | 99 | 27
Ontario | Temagami | Ontario Temagami | 300 | 47.07 | -79.78 | –33 | 89 | 23
Ontario | Thamesford | Ontario Thamesford | 280 | 43.07 | -81 | –21 | 99 | 30
Ontario | Thedford | Ontario Thedford | 205 | 43.15 | -81.85 | –18 | 106 | 22
Ontario | Thunder Bay | Ontario Thunder Bay | 210 | 48.4 | -89.32 | –33 | 93 | 18
Ontario | Tillsonburg | Ontario Tillsonburg | 215 | 42.85 | -80.73 | –19 | 100 | 30
Ontario | Timmins | Ontario Timmins | 300 | 48.47 | -81.33 | –36 | 89 | 18
Ontario | Timmins (Porcupine) | Ontario Timmins (Porcupine) | 295 | 48.5 | -81.17 | –36 | 89 | 18
Toronto Area | Etobicoke | Toronto Area Etobicoke | 160 | 43.7 | -79.57 | –22 | 99 | 25
Toronto Area | North York | Toronto Area North York | 175 | 43.77 | -79.42 | –22 | 99 | 25
Toronto Area | Scarborough | Toronto Area Scarborough | 180 | 43.78 | -79.25 | –22 | 99 | 21
Toronto Area | Toronto (City Hall) | Toronto Area Toronto (City Hall) | 90 | 43.65 | -79.38 | –20 | 100 | 23
Toronto Area | Toronto (LBP Int’l Airport) | Toronto Area Toronto (LBP Int’l Airport) | 170 | 43.68 | -79.61 | –22 | 99 | 23
Toronto Area | Trenton | Toronto Area Trenton | 80 | 44.1 | -77.58 | –24 | 103 | 21
Toronto Area | Trout Creek | Toronto Area Trout Creek | 330 | 45.98 | -79.37 | –29 | 80 | 22
Toronto Area | Uxbridge | Toronto Area Uxbridge | 275 | 44.1 | -79.12 | –24 | 98 | 25
Toronto Area | Vaughan (Woodbridge) | Toronto Area Vaughan (Woodbridge) | 165 | 43.78 | -79.6 | –22 | 99 | 25
Toronto Area | Vittoria | Toronto Area Vittoria | 215 | 42.77 | -80.32 | –17 | 103 | 33
Toronto Area | Walkerton | Toronto Area Walkerton | 275 | 44.12 | -81.15 | –20 | 99 | 23
Toronto Area | Wallaceburg | Toronto Area Wallaceburg | 180 | 42.6 | -82.38 | –18 | 99 | 25
Toronto Area | Waterloo | Toronto Area Waterloo | 330 | 43.47 | -80.52 | –21 | 91 | 26
Toronto Area | Watford | Toronto Area Watford | 240 | 42.95 | -81.88 | –19 | 99 | 24
Toronto Area | Wawa | Toronto Area Wawa | 290 | 47.98 | -84.78 | –36 | 90 | 20
Toronto Area | Welland | Toronto Area Welland | 180 | 42.98 | -79.25 | –17 | 100 | 28
Toronto Area | West Lorne | Toronto Area West Lorne | 215 | 42.6 | -81.6 | –18 | 99 | 28
Toronto Area | Whitby | Toronto Area Whitby | 85 | 43.87 | -78.93 | –22 | 104 | 20
Toronto Area | Whitby (Brooklin) | Toronto Area Whitby (Brooklin) | 160 | 43.95 | -78.95 | –22 | 99 | 20
Toronto Area | White River | Toronto Area White River | 375 | 48.6 | -85.28 | –42 | 83 | 13
Toronto Area | Wiarton | Toronto Area Wiarton | 185 | 44.75 | -81.15 | –21 | 100 | 18
Toronto Area | Windsor | Toronto Area Windsor | 185 | 42.3 | -83.02 | –18 | 99 | 25
Toronto Area | Wingham | Toronto Area Wingham | 310 | 43.88 | -81.32 | –20 | 106 | 23
Toronto Area | Woodstock | Toronto Area Woodstock | 300 | 43.13 | -80.75 | –21 | 99 | 28
Toronto Area | Wyoming | Toronto Area Wyoming | 215 | 42.95 | -82.12 | –18 | 100 | 24
Québec | Acton–Vale | Québec Acton–Vale | 95 | 45.65 | -72.57 | –27 | 89 | 26
Québec | Alma | Québec Alma | 110 | 48.55 | -71.65 | –33 | 91 | 25
Québec | Amos | Québec Amos | 295 | 48.57 | -78.12 | –36 | 80 | 16
Québec | Asbestos | Québec Asbestos | 245 | 45.77 | -71.93 | –28 | 80 | 25
Québec | Aylmer | Québec Aylmer | 90 | 45.4 | -75.83 | –28 | 96 | 27
Québec | Baie–Comeau | Québec Baie–Comeau | 60 | 49.22 | -68.15 | –29 | 106 | 25
Québec | Baie–Saint–Paul | Québec Baie–Saint–Paul | 20 | 47.44 | -70.51 | –29 | 99 | 27
Québec | Beauport | Québec Beauport | 45 | 46.87 | -71.18 | –29 | 98 | 30
Québec | Bedford | Québec Bedford | 55 | 45.12 | -72.98 | –26 | 89 | 26
Québec | Beloeil | Québec Beloeil | 25 | 45.57 | -73.2 | –26 | 91 | 32
Québec | Brome | Québec Brome | 210 | 45.2 | -72.57 | –27 | 80 | 27
Québec | Brossard | Québec Brossard | 15 | 45.45 | -73.47 | –26 | 98 | 32
Québec | Buckingham | Québec Buckingham | 130 | 45.58 | -75.42 | –28 | 95 | 30
Québec | Campbell’s Bay | Québec Campbell’s Bay | 115 | 45.73 | -76.6 | –30 | 85 | 25
Québec | Chambly | Québec Chambly | 20 | 45.45 | -73.28 | –26 | 95 | 30
Québec | Coaticook | Québec Coaticook | 295 | 45.13 | -71.8 | –27 | 80 | 20
Québec | Contrecœur | Québec Contrecœur | 10 | 45.85 | -73.23 | –27 | 99 | 30
Québec | Cowansville | Québec Cowansville | 120 | 45.2 | -72.75 | –27 | 80 | 28
Québec | Deux–Montagnes | Québec Deux–Montagnes | 25 | 45.53 | -73.88 | –27 | 91 | 32
Québec | Dolbeau | Québec Dolbeau | 120 | 48.88 | -72.23 | –34 | 91 | 25
Québec | Drummondville | Québec Drummondville | 85 | 45.88 | -72.48 | –28 | 89 | 28
Québec | Farnham | Québec Farnham | 60 | 45.28 | -72.98 | –26 | 89 | 28
Québec | Fort–Coulonge | Québec Fort–Coulonge | 110 | 45.85 | -76.73 | –30 | 85 | 24
Québec | Gagnon | Québec Gagnon | 545 | 51.93 | -68.17 | –36 | 93 | 18
Québec | Gaspé | Québec Gaspé | 55 | 48.83 | -64.48 | –26 | 100 | 25
Québec | Gatineau | Québec Gatineau | 95 | 45.5 | -75.65 | –28 | 96 | 30
Québec | Gracefield | Québec Gracefield | 175 | 46.1 | -76.05 | –31 | 85 | 25
Québec | Granby | Québec Granby | 120 | 45.4 | -72.73 | –27 | 89 | 28
Québec | Harrington–Harbour | Québec Harrington–Harbour | 30 | 50.5 | -59.48 | –29 | 127 | 30
Québec | Havre–St–Pierre | Québec Havre–St–Pierre | 5 | 50.23 | -63.6 | –29 | 119 | 28
Québec | Hemmingford | Québec Hemmingford | 75 | 45.05 | -73.58 | –26 | 89 | 30
Québec | Hull | Québec Hull | 65 | 45.43 | -75.73 | –28 | 90 | 30
Québec | Iberville | Québec Iberville | 35 | 45.35 | -73.23 | –26 | 89 | 30
Québec | Inukjuak | Québec Inukjuak | 5 | 58.48 | -78.1 | –38 | 109 | 12
Québec | Joliette | Québec Joliette | 45 | 46.02 | -73.45 | –28 | 90 | 30
Québec | Kuujjuaq | Québec Kuujjuaq | 25 | 58.1 | -68.4 | –39 | 117 | 12
Québec | Kuujjuarapik | Québec Kuujjuarapik | 20 | 55.28 | -77.75 | –38 | 105 | 12
Québec | La Pocatière | Québec La Pocatière | 55 | 47.37 | -70.04 | –26 | 99 | 27
Québec | Lachute | Québec Lachute | 65 | 45.65 | -74.33 | –28 | 95 | 32
Québec | Lac–Mégantic | Québec Lac–Mégantic | 420 | 45.58 | -70.88 | –29 | 80 | 23
Québec | La–Malbaie | Québec La–Malbaie | 25 | 47.65 | -70.15 | –28 | 104 | 26
Québec | La–Tuque | Québec La–Tuque | 165 | 47.43 | -72.78 | –32 | 89 | 24
Québec | Lennoxville | Québec Lennoxville | 155 | 45.37 | -71.85 | –30 | 80 | 20
Québec | Léry | Québec Léry | 30 | 45.35 | -73.8 | –26 | 98 | 32
Québec | Loretteville | Québec Loretteville | 100 | 46.85 | -71.35 | –29 | 96 | 30
Québec | Louiseville | Québec Louiseville | 15 | 46.25 | -72.95 | –28 | 99 | 30
Québec | Magog | Québec Magog | 215 | 45.27 | -72.13 | –28 | 80 | 20
Québec | Malartic | Québec Malartic | 325 | 48.13 | -78.13 | –36 | 80 | 18
Québec | Maniwaki | Québec Maniwaki | 180 | 46.38 | -75.97 | –32 | 84 | 25
Québec | Masson | Québec Masson | 50 | 45.53 | -75.42 | –28 | 95 | 30
Québec | Matane | Québec Matane | 5 | 48.85 | -67.53 | –26 | 110 | 27
Québec | Mont–Joli | Québec Mont–Joli | 90 | 48.58 | -68.18 | –26 | 108 | 27
Québec | Mont–Laurier | Québec Mont–Laurier | 225 | 46.55 | -75.5 | –32 | 83 | 22
Québec | Montmagny | Québec Montmagny | 10 | 46.98 | -70.55 | –28 | 99 | 29
Montréal Area | Beaconsfield | Montréal Area Beaconsfield | 25 | 45.43 | -73.87 | –26 | 98 | 32
Montréal Area | Dorval | Montréal Area Dorval | 25 | 45.45 | -73.75 | –26 | 98 | 32
Montréal Area | Laval | Montréal Area Laval | 35 | 45.58 | -73.75 | –26 | 98 | 32
Montréal Area | Montréal (City Hall) | Montréal Area Montréal (City Hall) | 20 | 45.51 | -73.55 | –26 | 98 | 32
Montréal Area | Montréal–Est | Montréal Area Montréal–Est | 25 | 45.63 | -73.52 | –26 | 98 | 32
Montréal Area | Montréal–Nord | Montréal Area Montréal–Nord | 20 | 45.6 | -73.63 | –26 | 98 | 32
Montréal Area | Outremont | Montréal Area Outremont | 105 | 45.52 | -73.62 | –26 | 98 | 32
Montréal Area | Pierrefonds | Montréal Area Pierrefonds | 25 | 45.48 | -73.87 | –26 | 98 | 32
Montréal Area | St–Lambert | Montréal Area St–Lambert | 15 | 45.5 | -73.5 | –26 | 98 | 32
Montréal Area | St–Laurent | Montréal Area St–Laurent | 45 | 45.5 | -73.67 | –26 | 98 | 32
Montréal Area | Ste–Anne–de–Bellevue | Montréal Area Ste–Anne–de–Bellevue | 35 | 45.42 | -73.93 | –26 | 98 | 32
Montréal Area | Verdun | Montréal Area Verdun | 20 | 45.45 | -73.57 | –26 | 98 | 32
Montréal Area | Nicolet (Gentilly) | Montréal Area Nicolet (Gentilly) | 15 | 46.4 | -72.28 | –28 | 98 | 30
Montréal Area | Nitchequon | Montréal Area Nitchequon | 545 | 53.21 | -70.91 | –41 | 90 | 15
Montréal Area | Noranda | Montréal Area Noranda | 305 | 48.25 | -79.02 | –36 | 80 | 18
Montréal Area | Percé | Montréal Area Percé | 5 | 48.53 | -64.22 | –24 | 120 | 28
Montréal Area | Pincourt | Montréal Area Pincourt | 25 | 45.38 | -73.98 | –26 | 98 | 30
Montréal Area | Plessisville | Montréal Area Plessisville | 145 | 46.22 | -71.78 | –28 | 89 | 27
Montréal Area | Port–Cartier | Montréal Area Port–Cartier | 20 | 50.02 | -66.87 | –30 | 110 | 25
Montréal Area | Puvinrituq | Montréal Area Puvinrituq | 5 | 60.03 | -77.28 | –38 | 117 | 10
Québec and environs | Ancienne–Lorette | Québec and environs Ancienne–Lorette | 35 | 46.78 | -71.38 | –28 | 96 | 30
Québec and environs | Lévis | Québec and environs Lévis | 50 | 46.8 | -71.18 | –28 | 96 | 30
Québec and environs | Québec | Québec and environs Québec | 120 | 46.8 | -71.23 | –28 | 96 | 30
Québec and environs | Sillery | Québec and environs Sillery | 10 | 46.77 | -71.25 | –28 | 96 | 30
Québec and environs | Ste–Foy | Québec and environs Ste–Foy | 115 | 46.78 | -71.28 | –28 | 96 | 30
Québec | Richmond | Québec Richmond | 150 | 45.67 | -72.15 | –27 | 80 | 26
Québec | Rimouski | Québec Rimouski | 30 | 48.43 | -68.55 | –27 | 108 | 27
Québec | Rivière–du–Loup | Québec Rivière–du–Loup | 55 | 47.83 | -69.53 | –27 | 106 | 25
Québec | Roberval | Québec Roberval | 100 | 48.52 | -72.23 | –33 | 91 | 23
Québec | Rock–Island | Québec Rock–Island | 160 | 45.04 | -72.1 | –27 | 80 | 20
Québec | Rosemère | Québec Rosemère | 25 | 45.63 | -73.8 | –26 | 95 | 32
Québec | Rouyn | Québec Rouyn | 300 | 48.23 | -79.02 | –36 | 80 | 18
Québec | Saguenay | Québec Saguenay | 10 | 48.43 | -71.07 | –32 | 91 | 25
Québec | Saguenay (Bagotville) | Québec Saguenay (Bagotville) | 5 | 48.35 | -70.88 | –33 | 92 | 25
Québec | Saguenay (Jonquière) | Québec Saguenay (Jonquière) | 135 | 48.42 | -71.22 | –32 | 91 | 25
Québec | Saguenay (Kénogami) | Québec Saguenay (Kénogami) | 140 | 48.42 | -71.25 | –32 | 91 | 25
Québec | Saint–Eustache | Québec Saint–Eustache | 35 | 45.56 | -73.9 | –27 | 91 | 32
Québec | Saint–Jean–sur–Richelieu | Québec Saint–Jean–sur–Richelieu | 35 | 45.31 | -73.26 | –26 | 89 | 30
Québec | Salaberry–de–Valleyfield | Québec Salaberry–de–Valleyfield | 50 | 45.25 | -74.13 | –25 | 98 | 32
Québec | Schefferville | Québec Schefferville | 550 | 54.8 | -66.83 | –39 | 102 | 15
Québec | Senneterre | Québec Senneterre | 310 | 48.38 | -77.23 | –36 | 80 | 18
Québec | Sept–Îles | Québec Sept–Îles | 5 | 50.2 | -66.38 | –31 | 110 | 25
Québec | Shawinigan | Québec Shawinigan | 60 | 46.55 | -72.75 | –29 | 89 | 30
Québec | Shawville | Québec Shawville | 170 | 45.6 | -76.48 | –30 | 89 | 25
Québec | Sherbrooke | Québec Sherbrooke | 185 | 45.42 | -71.9 | –30 | 80 | 20
Québec | Sorel | Québec Sorel | 10 | 46.03 | -73.12 | –27 | 99 | 30
Québec | Ste–Agathe–des–Monts | Québec Ste–Agathe–des–Monts | 360 | 46.05 | -74.28 | –30 | 89 | 24
Québec | St–Félicien | Québec St–Félicien | 105 | 48.65 | -72.45 | –34 | 91 | 25
Québec | St–Georges–de–Cacouna | Québec St–Georges–de–Cacouna | 35 | 47.92 | -69.5 | –27 | 106 | 25
Québec | St–Hubert | Québec St–Hubert | 25 | 45.5 | -73.42 | –26 | 98 | 32
Québec | St–Hubert–de–Rivière–du–Loup | Québec St–Hubert–de–Rivière–du–Loup | 310 | 47.82 | -69.15 | –28 | 95 | 25
Québec | St–Hyacinthe | Québec St–Hyacinthe | 35 | 45.62 | -72.95 | –27 | 89 | 30
Québec | St–Jérôme | Québec St–Jérôme | 95 | 45.78 | -74 | –28 | 91 | 30
Québec | St–Jovite | Québec St–Jovite | 230 | 46.12 | -74.6 | –31 | 86 | 25
Québec | St–Lazare–Hudson | Québec St–Lazare–Hudson | 60 | 45.4 | -74.14 | –26 | 98 | 30
Québec | St–Nicolas | Québec St–Nicolas | 65 | 46.7 | -71.4 | –28 | 98 | 30
Québec | Sutton | Québec Sutton | 185 | 45.1 | -72.62 | –27 | 80 | 26
Québec | Tadoussac | Québec Tadoussac | 65 | 48.15 | -69.72 | –28 | 108 | 25
Québec | Témiscaming | Québec Témiscaming | 240 | 46.72 | -79.1 | –32 | 85 | 22
Québec | Terrebonne | Québec Terrebonne | 20 | 45.69 | -73.63 | –27 | 94 | 30
Québec | Thetford Mines | Québec Thetford Mines | 330 | 46.08 | -71.3 | –28 | 80 | 25
Québec | Thurso | Québec Thurso | 50 | 45.6 | -75.25 | –28 | 95 | 30
Québec | Trois–Rivières | Québec Trois–Rivières | 25 | 46.35 | -72.55 | –28 | 99 | 30
Québec | Val–d’Or | Québec Val–d’Or | 310 | 48.1 | -77.78 | –36 | 80 | 18
Québec | Varennes | Québec Varennes | 15 | 45.68 | -73.43 | –26 | 95 | 30
Québec | Verchères | Québec Verchères | 15 | 45.78 | -73.35 | –26 | 99 | 30
Québec | Victoriaville | Québec Victoriaville | 125 | 46.05 | -71.97 | –28 | 89 | 28
Québec | Ville–Marie | Québec Ville–Marie | 200 | 47.33 | -79.43 | –34 | 89 | 22
Québec | Wakefield | Québec Wakefield | 120 | 45.64 | -75.93 | –30 | 88 | 25
Québec | Waterloo | Québec Waterloo | 205 | 45.35 | -72.52 | –27 | 80 | 26
Québec | Windsor | Québec Windsor | 150 | 45.57 | -72 | –27 | 80 | 25
New Brunswick | Alma | New Brunswick Alma | 5 | 45.6 | -64.95 | –23 | 104 | 27
New Brunswick | Bathurst | New Brunswick Bathurst | 10 | 47.6 | -65.65 | –26 | 100 | 26
New Brunswick | Campbellton | New Brunswick Campbellton | 30 | 48 | -66.67 | –28 | 98 | 25
New Brunswick | Edmundston | New Brunswick Edmundston | 160 | 47.37 | -68.33 | –29 | 80 | 25
New Brunswick | Fredericton | New Brunswick Fredericton | 15 | 45.95 | -66.65 | –27 | 92 | 25
New Brunswick | Gagetown | New Brunswick Gagetown | 20 | 45.79 | -66.16 | –26 | 95 | 25
New Brunswick | Grand Falls | New Brunswick Grand Falls | 115 | 47.05 | -67.73 | –30 | 89 | 24
New Brunswick | Miramichi | New Brunswick Miramichi | 5 | 47.03 | -65.47 | –26 | 96 | 28
New Brunswick | Moncton | New Brunswick Moncton | 20 | 46.1 | -64.78 | –25 | 106 | 32
New Brunswick | Oromocto | New Brunswick Oromocto | 20 | 45.84 | -66.48 | –26 | 93 | 25
New Brunswick | Sackville | New Brunswick Sackville | 15 | 45.88 | -64.37 | –24 | 105 | 32
New Brunswick | Saint Andrews | New Brunswick Saint Andrews | 35 | 45.07 | -67.05 | –24 | 98 | 26
New Brunswick | Saint George | New Brunswick Saint George | 35 | 45.13 | -66.82 | –23 | 98 | 26
New Brunswick | Saint John | New Brunswick Saint John | 5 | 45.27 | -66.05 | –24 | 100 | 26
New Brunswick | Shippagan | New Brunswick Shippagan | 5 | 47.73 | -64.7 | –24 | 119 | 28
New Brunswick | St. Stephen | New Brunswick St. Stephen | 20 | 45.2 | -67.28 | –26 | 96 | 25
New Brunswick | Woodstock | New Brunswick Woodstock | 60 | 46.16 | -67.6 | –29 | 89 | 23
Nova Scotia | Amherst | Nova Scotia Amherst | 25 | 45.83 | -64.2 | –24 | 104 | 30
Nova Scotia | Antigonish | Nova Scotia Antigonish | 10 | 45.62 | -62 | –20 | 109 | 30
Nova Scotia | Bridgewater | Nova Scotia Bridgewater | 10 | 44.38 | -64.52 | –17 | 106 | 30
Nova Scotia | Canso | Nova Scotia Canso | 5 | 45.33 | -61 | –15 | 118 | 30
Nova Scotia | Dartmouth | Nova Scotia Dartmouth | 10 | 44.67 | -63.57 | –18 | 110 | 31
Nova Scotia | Debert | Nova Scotia Debert | 45 | 45.43 | -63.47 | –24 | 104 | 27
Nova Scotia | Digby | Nova Scotia Digby | 35 | 44.62 | -65.77 | –17 | 110 | 22
Nova Scotia | Greenwood (CFB) | Nova Scotia Greenwood (CFB) | 28 | 44.98 | -64.9 | –20 | 110 | 22
Nova Scotia | Halifax | Nova Scotia Halifax | 55 | 44.65 | -63.6 | –18 | 110 | 31
Nova Scotia | Kentville | Nova Scotia Kentville | 25 | 45.08 | -64.5 | –20 | 110 | 26
Nova Scotia | Liverpool | Nova Scotia Liverpool | 20 | 44.03 | -64.72 | –18 | 118 | 30
Nova Scotia | Lockeport | Nova Scotia Lockeport | 5 | 43.7 | -65.12 | –16 | 117 | 30
Nova Scotia | Louisburg | Nova Scotia Louisburg | 5 | 45.92 | -59.98 | –17 | 121 | 32
Nova Scotia | Lunenburg | Nova Scotia Lunenburg | 25 | 44.38 | -64.32 | –17 | 108 | 30
Nova Scotia | New Glasgow | Nova Scotia New Glasgow | 30 | 45.58 | -62.65 | –21 | 109 | 30
Nova Scotia | North Sydney | Nova Scotia North Sydney | 20 | 46.22 | -60.25 | –19 | 110 | 32
Nova Scotia | Pictou | Nova Scotia Pictou | 25 | 45.68 | -62.72 | –21 | 109 | 30
Nova Scotia | Port Hawkesbury | Nova Scotia Port Hawkesbury | 40 | 45.62 | -61.35 | –19 | 109 | 30
Nova Scotia | Springhill | Nova Scotia Springhill | 185 | 45.65 | -64.05 | –23 | 104 | 28
Nova Scotia | Stewiacke | Nova Scotia Stewiacke | 25 | 45.13 | -63.35 | –22 | 106 | 28
Nova Scotia | Sydney | Nova Scotia Sydney | 5 | 46.15 | -60.18 | –19 | 110 | 32
Nova Scotia | Tatamagouche | Nova Scotia Tatamagouche | 25 | 45.72 | -63.3 | –23 | 109 | 30
Nova Scotia | Truro | Nova Scotia Truro | 25 | 45.37 | -63.27 | –22 | 104 | 29
Nova Scotia | Wolfville | Nova Scotia Wolfville | 35 | 45.08 | -64.37 | –21 | 110 | 27
Nova Scotia | Yarmouth | Nova Scotia Yarmouth | 10 | 43.83 | -66.12 | –16 | 112 | 25
Nova Scotia | Charlottetown | Nova Scotia Charlottetown | 5 | 46.23 | -63.13 | –22 | 112 | 30
Nova Scotia | Souris | Nova Scotia Souris | 5 | 46.35 | -62.25 | –21 | 114 | 30
Nova Scotia | Summerside | Nova Scotia Summerside | 10 | 46.4 | -63.78 | –22 | 114 | 30
Nova Scotia | Tignish | Nova Scotia Tignish | 10 | 46.95 | -64.03 | –22 | 122 | 30
Newfoundland and Labrador | Argentia | Newfoundland and Labrador Argentia | 15 | 47.3 | -53.98 | –14 | 130 | 35
Newfoundland and Labrador | Bonavista | Newfoundland and Labrador Bonavista | 15 | 48.65 | -53.12 | –16 | 140 | 40
Newfoundland and Labrador | Buchans | Newfoundland and Labrador Buchans | 255 | 48.82 | -56.87 | –27 | 115 | 24
Newfoundland and Labrador | Cape Harrison | Newfoundland and Labrador Cape Harrison | 5 | 54.78 | -57.95 | –31 | 130 | 35
Newfoundland and Labrador | Cape Race | Newfoundland and Labrador Cape Race | 5 | 46.65 | -53.07 | –13 | 154 | 45
Newfoundland and Labrador | Channel–Port aux Basques | Newfoundland and Labrador Channel–Port aux Basques | 5 | 47.57 | -59.15 | –15 | 133 | 32
Newfoundland and Labrador | Corner Brook | Newfoundland and Labrador Corner Brook | 35 | 48.95 | -57.95 | –18 | 111 | 24
Newfoundland and Labrador | Gander | Newfoundland and Labrador Gander | 125 | 48.98 | -54.59 | –20 | 117 | 30
Newfoundland and Labrador | Grand Bank | Newfoundland and Labrador Grand Bank | 5 | 47.1 | -55.77 | –15 | 130 | 35
Newfoundland and Labrador | Grand Falls | Newfoundland and Labrador Grand Falls | 60 | 48.93 | -55.67 | –29 | 100 | 28
Newfoundland and Labrador | Happy Valley–Goose Bay | Newfoundland and Labrador Happy Valley–Goose Bay | 15 | 53.32 | -60.37 | –32 | 98 | 20
Newfoundland and Labrador | Labrador City | Newfoundland and Labrador Labrador City | 550 | 52.95 | -66.92 | –38 | 95 | 15
Newfoundland and Labrador | St. Anthony | Newfoundland and Labrador St. Anthony | 10 | 51.37 | -55.58 | –27 | 138 | 30
Newfoundland and Labrador | St. John’s | Newfoundland and Labrador St. John’s | 65 | 47.57 | -52.72 | –16 | 138 | 42
Newfoundland and Labrador | Stephenville | Newfoundland and Labrador Stephenville | 25 | 48.55 | -58.58 | –18 | 114 | 24
Newfoundland and Labrador | Twin Falls | Newfoundland and Labrador Twin Falls | 425 | 53.5 | -64.53 | –37 | 95 | 17
Newfoundland and Labrador | Wabana | Newfoundland and Labrador Wabana | 75 | 47.63 | -52.95 | –17 | 130 | 40
Newfoundland and Labrador | Wabush | Newfoundland and Labrador Wabush | 550 | 52.92 | -66.87 | –38 | 95 | 15
Yukon | Aishihik | Yukon Aishihik | 920 | 61.6 | -137.52 | –46 | 85 | 10
Yukon | Dawson | Yukon Dawson | 330 | 64.07 | -139.42 | –51 | 80 | 10
Yukon | Destruction Bay | Yukon Destruction Bay | 815 | 61.25 | -138.8 | –45 | 117 | 10
Yukon | Faro | Yukon Faro | 670 | 62.23 | -133.36 | –47 | 80 | 10
Yukon | Haines Junction | Yukon Haines Junction | 600 | 60.78 | -137.54 | –47 | 87 | 10
Yukon | Snag | Yukon Snag | 595 | 62.4 | -140.37 | –53 | 80 | 10
Yukon | Teslin | Yukon Teslin | 690 | 60.17 | -132.72 | –44 | 80 | 10
Yukon | Watson Lake | Yukon Watson Lake | 685 | 60.13 | -128.71 | –48 | 80 | 10
Yukon | Whitehorse | Yukon Whitehorse | 655 | 60.72 | -135.05 | –43 | 85 | 10
Northwest Territories | Aklavik | Northwest Territories Aklavik | 5 | 68.23 | -135.01 | –44 | 100 | 10
Northwest Territories | Echo Bay / Port Radium | Northwest Territories Echo Bay / Port Radium | 195 | 66.05 | -117.88 | –44 | 99 | 10
Northwest Territories | Fort Good Hope | Northwest Territories Fort Good Hope | 100 | 66.29 | -128.63 | –45 | 89 | 10
Northwest Territories | Fort McPherson | Northwest Territories Fort McPherson | 25 | 67.43 | -134.88 | –46 | 90 | 10
Northwest Territories | Fort Providence | Northwest Territories Fort Providence | 150 | 61.35 | -117.65 | –43 | 80 | 10
Northwest Territories | Fort Resolution | Northwest Territories Fort Resolution | 160 | 61.19 | -113.67 | –42 | 93 | 10
Northwest Territories | Fort Simpson | Northwest Territories Fort Simpson | 120 | 61.93 | -121.35 | –44 | 80 | 10
Northwest Territories | Fort Smith | Northwest Territories Fort Smith | 205 | 60 | -111.88 | –43 | 80 | 10
Northwest Territories | Hay River | Northwest Territories Hay River | 45 | 60.85 | -115.73 | –41 | 89 | 10
Northwest Territories | Inuvik | Northwest Territories Inuvik | 45 | 68.35 | -133.72 | –45 | 100 | 10
Northwest Territories | Mould Bay | Northwest Territories Mould Bay | 5 | 76.23 | -119.33 | –46 | 114 | 10
Northwest Territories | Norman Wells | Northwest Territories Norman Wells | 65 | 65.28 | -126.85 | –45 | 89 | 10
Northwest Territories | Rae–Edzo | Northwest Territories Rae–Edzo | 160 | 62.83 | -116.05 | –44 | 103 | 10
Northwest Territories | Tungsten | Northwest Territories Tungsten | 1340 | 61.95 | -128.27 | –51 | 90 | 10
Northwest Territories | Ulukhaqtuuq/Holman | Northwest Territories Ulukhaqtuuq/Holman | 10 | 70.73 | -117.75 | –41 | 120 | 10
Northwest Territories | Wrigley | Northwest Territories Wrigley | 80 | 63.23 | -123.47 | –44 | 80 | 10
Northwest Territories | Yellowknife | Northwest Territories Yellowknife | 160 | 62.48 | -114.35 | –44 | 103 | 10
Nunavut | Alert | Nunavut Alert | 5 | 82.48 | -62.25 | –44 | 130 | 10
Nunavut | Arctic Bay | Nunavut Arctic Bay | 15 | 73.03 | -85.17 | –44 | 111 | 10
Nunavut | Arviat | Nunavut Arviat | 5 | 61.12 | -94.05 | –41 | 114 | 10
Nunavut | Baker Lake | Nunavut Baker Lake | 5 | 64.32 | -96.02 | –44 | 110 | 10
Nunavut | Eureka | Nunavut Eureka | 5 | 79.98 | -85.95 | –48 | 110 | 10
Nunavut | Igluligaarjuk/Chesterfield Inlet | Nunavut Igluligaarjuk/Chesterfield Inlet | 10 | 63.33 | -90.7 | –41 | 112 | 10
Nunavut | Iqaluit | Nunavut Iqaluit | 45 | 63.73 | -68.5 | –41 | 114 | 10
Nunavut | Iqaluktuuttiaq/Cambridge Bay | Nunavut Iqaluktuuttiaq/Cambridge Bay | 15 | 69.12 | -105.03 | –44 | 110 | 10
Nunavut | Isachsen | Nunavut Isachsen | 10 | 78.78 | -103.53 | –48 | 117 | 10
Nunavut | Kangiqiniq/Rankin Inlet | Nunavut Kangiqiniq/Rankin Inlet | 10 | 62.82 | -92.08 | –42 | 117 | 10
Nunavut | Kanngiqtugaapik/Clyde River | Nunavut Kanngiqtugaapik/Clyde River | 5 | 70.45 | -68.57 | –42 | 127 | 10
Nunavut | Kugluktuk | Nunavut Kugluktuk | 10 | 67.83 | -115.08 | –43 | 102 | 10
Nunavut | Nottingham Island | Nunavut Nottingham Island | 30 | 63.1 | -78 | –39 | 133 | 10
Nunavut | Resolute | Nunavut Resolute | 25 | 74.68 | -94.9 | –43 | 119 | 10
Nunavut | Resolution Island | Nunavut Resolution Island | 5 | 61.3 | -64.88 | –34 | 166 | 10
Nunavut | Salliq/Coral Harbour | Nunavut Salliq/Coral Harbour | 15 | 64.13 | -83.17 | –42 | 118 | 10